## Deficiency Tracker
E&I DEFICIENCY TRACKER
Use filters to sort by area, system, priority, responsible party, due date, or status. Blue cells are user-entry fields; grey cells calculate automatically.
Project: | K1B Wellpad Proj. | Contractor: | Yanda | Prepared By: | Levy Ostrup | Client: COOEC | COOEC | Location: | K1B Wellpad Project | Last Updated: | 01-10-2026 | Open: | 149 | Overdue: | 6 | Ready for Verification: | 0 | Closed: | 34
Deficiency ID | Date Identified | Area / Module | System | Discipline | Tag / Equipment No. | Drawing / EWP / ITR Ref. | Category | Deficiency Description | Priority | Responsible Party | Target Date | Status | Date Corrected | Verified By | Verification Date | Days Open | Overdue? | Photo / NCR / RFI Ref. | Comments / Close-out Details
DEF-0003 | 2026-07-21 | WPM-104 | K1A-600V | Electrical | 29103-HTP-003 |  | Code / Standard | Cables need supporting under controller | Medium | Construction | 2026-07-30 | Open |  |  |  | 60 | Yes
DEF-0004 | 2026-07-15 | WPM-104 | K1A-600V / EHT | Electrical | 29103-ET-PE1709-1-1 |  | Damage | Trace broken | High | Construction | 2026-07-30 | Open |  |  |  | 66 | Yes
QSR-K1B-038 | 2026-07-17 | A mods | K1B-600V | Electrical | 29103-LJB-103/102 |  | Code / Standard | LJB's missing lamacoids | Low | Construction | 2026-07-31 | Open |  |  |  | 64 | Yes | CA23007-QSR-K1B-038
QSR-K1B-039 | 2026-07-19 | A mods | K1B-600V / EHT | Electrical | EHT |  | Code / Standard | Inproper EHT installation | Medium | Construction | 2026-07-31 | Open |  |  |  | 62 | Yes | CA23007-QSR-K1B-039
DEF-0005 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-VD-P25,26,27 |  | Installation | Armour is showing on cable at connector (Inproper gland) | Medium | Construction |  | Open |  |  |  | 89
DEF-0006 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-ELM-101 |  | Code / Standard | Strut needs protective coating of Cold Galv. | Medium | Construction |  | Open |  |  |  | 89
DEF-0007 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-ELM-101 |  | Documentation | Vertical tray downs to be changed to match the rest. | Low | Construction |  | Open |  |  |  | 89
DEF-0008 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-ELM-101 |  | Code / Standard | All ground connections need Glyptol present. | Medium | Construction |  | Open |  |  |  | 89
DEF-0009 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-PT-P12 |  | Installation | Armour is showing on cable at connector (Inproper gland) | Medium | Construction |  | Open |  |  |  | 89
DEF-0010 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-ELM-101 |  | Code / Standard | Cable tags missing | Low | Construction |  | Open |  |  |  | 89
DEF-0011 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-VFD-P24 |  | Code / Standard | Missing Lamacoid on 29103-VFD-P24 | Low | Construction |  | Open |  |  |  | 89
DEF-0012 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-PT-P16 |  | Installation | Ground strain relief is cross threaded (Inproper Install), Add weatherproof washer | Low | Construction |  | Open |  |  |  | 89
DEF-0013 | 2026-06-22 | 29103-ELM-101 | K1B-600V-ESP | Electrical | 29103-ELM-101 |  | Installation | Cobra clamps on VFD feed are wrong size | Low | Construction |  | Open |  |  |  | 89
DEF-0014 | 2026-06-18 | 29103-WPM-102 |  | Electrical | PE1202-1-PWK-1 |  | Documentation | MI trace part number partially scratched | Low | Construction |  | Open |  |  |  | 93
DEF-0015 | 2026-06-18 | 29103-WPM-102 |  | Electrical | PG1401-1-R-2 |  | Code / Standard | RTD not secure, Need insulation stripped to re-secure | Low | Construction |  | Open |  |  |  | 93
DEF-0016 | 2026-06-18 | 29103-WPM-103 |  | Electrical | P1601-1-PWK-1 |  | Documentation | MI trace part number partially scratched | Low | Construction |  | Open |  |  |  | 93
DEF-0017 | 2026-06-18 | 29103-WPM-104 |  | Electrical | PE1602-1-PWK-1 |  | Code / Standard | Cable bend Radi is tight, Armour is present at connector | Low | Construction |  | Open |  |  |  | 93
DEF-0018 | 2026-06-18 | 29103-WPM-101/104 |  | Electrical | N/A |  | Code / Standard | Strut needs protective coating of Cold Galv. | Low | Construction |  | Open |  |  |  | 93
DEF-0019 | 2026-06-18 | 29103-WPM-101/104 |  | Electrical | N/A |  | Code / Standard | I-Tray needs grommet | Low | Construction |  | Open |  |  |  | 93
DEF-0020 | 2026-06-18 | 29103-WPM-104 |  | Electrical | PE1701-2-R-2 |  | Installation | Terminated in the wrong TB in 29103-HTP-003 | Low | Construction |  | Open |  |  |  | 93
DEF-0021 | 2026-07-18 |  | K1B-PE | Electrical | 29103-ET-PG1201-1-R-2 |  | Installation | Missing Cable for RTD | Medium | Construction |  | Open |  |  |  | 63
DEF-0022 | 2026-07-18 |  |  | Electrical | 29103-ET-P1204-1-1 |  | Installation | Missing Cable for RTD | Medium | Construction |  | Open |  |  |  | 63
DEF-0023 | 2026-07-18 |  | K1B-PE | Electrical | 29103-PE1404-1-R2-R |  | Installation | Missing Cable for RTD | Medium | Construction |  | Open |  |  |  | 63
DEF-0024 | 2026-07-18 |  | K1B-PE | Electrical | 29103-PE1701-1-1 |  | Installation | MI Trace is broken | Critical | Construction |  | Open |  |  |  | 63
DEF-0025 | 2026-07-18 | Stick built Prod. Wells | K1B-600V-ESP | Electrical | 29103-HVJB-P12 |  | Installation | Armour is showing on cable at connector (Inproper gland) | Medium | Construction |  | Open |  |  |  | 63
DEF-0026 | 2026-07-26 | 29209-EQM-103 | Multiple | Electrical | 29103-T-02-300-003 | 29103-65N-004-01 | Code / Standard | Tray ID's are not installed / Need Cold Galv on tray supports | Low | Construction |  | Open |  |  |  | 55
DEF-0027 | 2026-07-26 | 29209-EQM-103 | Multiple | Electrical | 29103-T-01-150-001 | 29103-65N-004-01 | Code / Standard | Tray ID's are not installed / Need Cold Galv on tray supports | Low | Construction |  | Open |  |  |  | 55
DEF-0028 | 2026-07-26 | 29209-EQM-103 | Multiple | Electrical | 29103-T-02-300-004 | 29103-65N-004-01 | Code / Standard | Tray ID's are not installed / Need Cold Galv on tray supports | Low | Construction |  | Open |  |  |  | 55
DEF-0029 | 2026-07-26 | 29209-EQM-103 | Multiple | Electrical | 29103-T-01-150-002 | 29103-65N-004-01 | Code / Standard | Tray ID's are not installed / Need Cold Galv on tray supports | Low | Construction |  | Open |  |  |  | 55
DEF-0030 | 2026-07-26 | 29209-EQM-103 | Multiple | Electrical | 29103-T-01-150-003 | 29103-65N-004-01 | Code / Standard | Tray ID's are not installed | Low | Construction |  | Open |  |  |  | 55
DEF-0031 | 2026-07-26 | Multiple | Multiple | Electrical | 29209-T-02-300-001 | 29103-65N-001-01 | Code / Standard | Missing Tray ID / C-Tap not taped | Low | Construction |  | In Progress |  |  |  | 55
DEF-0032 | 2026-07-26 | Multiple | Multiple | Electrical | 29103-T-01-150-001 | 29103-65N-001-01 | Code / Standard | Missing Tray ID / C-Tap not taped | Low | Construction |  | In Progress |  |  |  | 55
DEF-0033 | 2026-07-27 | 29103-CMM-201 | Multiple | Electrical | 29103-JJB-200 |  | Code / Standard | JBB needs lamacoid designation / Missing Main trunk cable | Low | Construction |  | Open |  |  |  | 54
DEF-0034 | 2026-07-27 | Multiple | Multiple | Electrical | 29103-JJB-XXX |  | Code / Standard | JJB's are missing termial strip marker designation | Low | Construction |  | Open |  |  |  | 54
DEF-0035 | 2026-07-25 | 29103-BDG-101 | K1B-600V-UPS | Electrical | 29103UPS-001-C |  | Code / Standard | Missing SS cable tag (MCC Side) | Low | Construction |  | Open |  |  |  | 56
DEF-0036 | 2026-07-25 | 29103-BDG-101 | K1B-600V-UPS | Instrumentation | 29103UP001-P |  | Code / Standard | Missing plastic bushing on both source and destination, Panel feeds require torqueing / marked | Medium | Construction |  | Open |  |  |  | 56
DEF-0037 | 2026-07-22 | 29103-BDG-101 | K1B-F&G | Electrical | 29103-XL-0900B | 29103-65N-203-01 | Code / Standard | Blue beacon, SS Cable tag is incorrect outside of I/A room | Low | Construction |  | Open |  |  |  | 59
DEF-0038 | 2026-07-22 | A Mods | Multiple | Electrical | 29103-XV-XXXX |  | Installation | Field run tray for XV's, cables were incorrecly drilled and supported through the side wall. | Low | Construction |  | Open |  |  |  | 59
DEF-0039 | 2026-07-22 | A Mods | K1B-HS | Electrical | 29103-ET-ST-1103-1-2 |  | Installation | EHT end bullet banding is coming off | Low | Construction |  | Open |  |  |  | 59
DEF-0040 | 2026-07-22 | A Mods | K1B-HS | Electrical | 29103-ET-ST-1103-1-1 |  | Installation | EHT is installed inproperly, (Wrapped around the Pipe) | Medium | Construction |  | Open |  |  |  | 59
DEF-0041 | 2026-07-23 | 29103-PRM-101 | K1B-600V-EHT | Electrical | 29103-HTT-100 |  | Code / Standard | Lamacoid is inproper | Low | Construction |  | Open |  |  |  | 58
DEF-0042 | 2026-07-29 | 29103-BDG-101 | N/A | Electrical | N/A | N/A | Housekeeping | MCC Front Deck (NGR): Ground cable lying on deck; secure/remove. | Low | Construction |  | Open |  |  |  | 52
DEF-0043 | 2026-07-29 | 29103-BDG-101 | N/A | Electrical | 29103-NGR001-C2 | N/A | Code / Standard | Missing tag | Low | Construction |  | Open |  |  |  | 52
DEF-0044 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | Up on scaffold strut weld should be cold galv painted | Low | Construction |  | Open |  |  |  | 52
DEF-0045 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | Most instrument tray bonds need to be glyptaled | Low | Construction |  | Open |  |  |  | 52
DEF-0046 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | 300mm tray requires an expansion joint, and tray splice needs additional support | Low | Construction |  | Open |  |  |  | 52
DEF-0047 | 2026-07-29 | 29103-BDG-101 | N/A | Electrical | N/A | N/A | Code / Standard | NGR Cable tags need to be changed to 9050-NGR-001-P AND 9050-NGR001-C1, 9050-NGR001-C2, 9050-NGR001-C3 | Low | Construction |  | Open |  |  |  | 52
DEF-0048 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | 300mm tray out to the pipe rack needs as strut installed for support | Low | Construction | Other | Open |  |  |  | 52 | #REF!
DEF-0049 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | 8' Vertical tray on south side drain, C-Tap not taped | Low | Construction |  | Open |  |  |  | 52
DEF-0050 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | A power kit cable missing ty-wrap | Low | Construction |  | Open |  |  |  | 52
DEF-0051 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Housekeeping | Cable ends need to be bagged and taped to prevent moisture and should be placed off ground | Low | Construction |  | Open |  |  |  | 52
DEF-0052 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | 29151-T-02-300-001 | N/A | Code / Standard | Missing tray ID'S | Low | Construction |  | Open |  |  |  | 52
DEF-0053 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | 29151-T-01-150-003 | N/A | Code / Standard | Missing tray ID'S | Low | Construction |  | Open |  |  |  | 52
DEF-0054 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | 29151-T-02-200-003 | N/A | Code / Standard | Missing tray ID'S | Low | Construction |  | Open |  |  |  | 52
DEF-0055 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | 29151-T-01-150-002 | N/A | Code / Standard | Missing tray ID'S | Low | Construction |  | Open |  |  |  | 52
DEF-0056 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | 29151-T-02-200-002 | N/A | Code / Standard | Missing tray ID'S | Low | Construction |  | Open |  |  |  | 52
DEF-0057 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | 29151-T-01-150-001 | N/A | Code / Standard | Missing tray ID'S | Low | Construction |  | Open |  |  |  | 52
DEF-0058 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | 29151-T-02-200-001 | N/A | Code / Standard | Missing tray ID'S | Low | Construction |  | Open |  |  |  | 52
DEF-0059 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | East of skid, ground cable outside of kick plate | Low | Construction |  | Open |  |  |  | 52
DEF-0060 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | Ground cable needs to be bonded | Medium | Construction |  | Open |  |  |  | 52
DEF-0061 | 2026-07-29 | 29151 Drain Area | N/A | Electrical | N/A | N/A | Code / Standard | Vertical tray south side, Ty-wraps need to be every second rung | Low | Construction |  | Open |  |  |  | 52
DEF-0062 | 2026-08-03 | 29103-BDG-101 | K1B-Ehouse | Electrical | 29103-BDG-101 | N/A | Code / Standard | Fire brick needed on all wall penetrations | Low | Construction | 2026-10-02 | Open |  |  |  | 47 | No
DEF-0063 | 2026-08-03 | 29103-BDG-101 | K2B-600V-EGEN | Electrical | 29103-BDG-101 | N/A | Code / Standard | GRL needs to be swapped out with Lock nuts and plastic bushing | High | Construction | 2026-08-04 | Open |  |  |  | 47 | Yes
DEF-0064 | 2026-08-03 | 29103-BDG-101 | K2B-600V-EGEN | Electrical | 29103-BDG-101 | N/A | Code / Standard | Scratch back pan around KA ground lugs to ensure continuity | High | Construction | 2026-08-04 | Open |  |  |  | 47 | Yes
DEF-0065 | 2026-08-15 |  | K1B-DCS-001 | Electrical | PIT-1012 | N/A | Installation | Loose connector | Medium | Construction |  | Open |  |  |  | 35
DEF-0066 | 2026-08-15 |  | K1B-DCS-001 | Electrical | FIT-1061 | N/A | Installation | Cables not Ty-raped in Tray / Support of cable from gland, distance is substantial. | Medium | Construction |  | Open |  |  |  | 35
DEF-0067 | 2026-08-15 |  | K1B-DCS-001 | Electrical | PIT-1062 | N/A | Installation | Cables not Ty-raped in Tray / Capilary lines need to be in I-Tray | Medium | Construction |  | Open |  |  |  | 35
DEF-0068 | 2026-08-15 |  | K1B-DCS-001 | Electrical | PIT-1072 | N/A | Installation | Incorrect Cable Tag | Medium | Construction |  | Open |  |  |  | 35
DEF-0069 | 2026-08-15 |  | K1B-DCS-001 | Electrical | FY-1072 | N/A | Installation | Core markers don’t match cable tag | Medium | Construction |  | Open |  |  |  | 35
DEF-0070 | 2026-08-15 |  | K1B-DCS-001 | Electrical | FY-1071 | N/A | Installation | Loose connector | Medium | Construction |  | Open |  |  |  | 35
DEF-0071 | 2026-08-15 |  | K1B-DCS-001 | Electrical | PIT-1071 | N/A | Installation | Missing cable tag | Medium | Construction |  | Open |  |  |  | 35
DEF-0072 | 2026-08-15 |  | K1B-DCS-001 | Electrical | FY-1061 | N/A | Installation | loose connector | Medium | Construction |  | Open |  |  |  | 35
DEF-0073 | 2026-08-15 |  | K1B-DCS-001 | Electrical | PIT-1061 | N/A | Installation | missing cable tag | Medium | Construction |  | Open |  |  |  | 35
DEF-0074 | 2026-08-15 |  | K1B-DCS-001 | Electrical | XY-1072 | N/A | Installation | missing cable tag / Wires are too long | Medium | Construction |  | Open |  |  |  | 35
DEF-0075 | 2026-08-15 |  | K1B-DCS-001 | Electrical | XY-1071 | N/A | Installation | Wires too long | Medium | Construction |  | Open |  |  |  | 35
DEF-0076 | 2026-08-15 |  | K1B-DCS-001 | Electrical | FIT--1074 | N/A | Installation | Cable tag missing | Medium | Construction |  | Open |  |  |  | 35
DEF-0077 | 2026-08-15 |  | K1B-DCS-001 | Electrical | XY-1072 | N/A | Installation | Missing cable tag, Wires are too long | Medium | Construction |  | Open |  |  |  | 35
DEF-0078 | 2026-08-15 |  | K1B-DCS-001 | Electrical | XY-1071 | N/A | Installation | Wires too long | Medium | Construction |  | Open |  |  |  | 35
DEF-0079 | 2026-08-15 |  | K1B-DCS-001 | Electrical | PIT-1012 | N/A | Installation | Connector loose | Medium | Construction |  | Open |  |  |  | 35
DEF-0080 | 2026-08-15 |  | K1B-DCS-001 | Electrical | PIT-1071 | N/A | Installation | Missing Cable tag | Medium | Construction |  | Open |  |  |  | 35
DEF-0081 | 2026-08-15 |  | K1B-DCS-001 | Electrical | PIT-1061 | N/A | Installation | Missing cable tag | Medium | Construction |  | Open |  |  |  | 35
DEF-0082 | 2026-08-15 | 29103-BDG-101 | K1B-600V-AHU | Electrical | MCC Air Handling Unit | N/A | Installation | Cable tags are missing under AHU | Medium | Construction |  | Open |  |  |  | 35
DEF-0083 | 2026-08-06 | 29209-EQM-101/102 | K1B-600V-SUS | Electrical | 29103-SB-001 | N/A | Installation | Splitter box need KO Filler / Cable needs support under tray. SS cable tags are missing on both field and source sides | High | Construction |  | Open |  |  |  | 44
DEF-0084 | 2026-08-20 |  | K1B-HS | Electrical | PIT-2172 |  | Installation | Wrong core marker | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2 |  |  | Completed by Dana
DEF-0085 | 2026-08-20 |  | K1B-HS | Electrical | PIT-2172 |  | Installation | Wrong Cable Tag | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0086 | 2026-08-20 |  | K1B-HS | Instrumentation | FY-1022 |  | Installation | IA Tubing support | Medium | Construction |  | Open |  |  |  | 30
DEF-0087 | 2026-08-20 |  | K1B-HS | Electrical | FIT-XXX |  | Installation | Dog tags on devices | Medium | Construction |  | Open |  |  |  | 30
DEF-0088 | 2026-08-20 |  | K1B-HS | Electrical | PIT-1031 |  | Installation | Upside down cable tag | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0089 | 2026-08-20 |  | K1B-HS | Instrumentation | PIT-1041 |  | Installation | Tighten U-Bolt | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0090 | 2026-08-20 |  | K1B-HS | Electrical | FY-1051 |  | Installation | Tags/Terms incomplete | Medium | Construction |  | Open |  |  |  | 30
DEF-0091 | 2026-08-20 |  | K1B-HS | Electrical | FY-1052 |  | Installation | Tags/Terms incomplete | Medium | Construction |  | Open |  |  |  | 30
DEF-0092 | 2026-08-20 |  | K1B-HS | Instrumentation | FIT-1061 |  | Installation | Tighten U-Bolt | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0093 | 2026-08-20 |  | K1B-HS | Electrical | PIT-1071 |  | Installation | No Cable tag present | Medium | Construction |  | Open |  |  |  | 30
DEF-0094 | 2026-08-20 |  | K1B-HS | Instrumentation | FIT-1071 |  | Installation | Loose U-Bolt | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0095 | 2026-08-20 |  | K1B-HS | Instrumentation | WPM-100/104 |  | Installation | Chop J-Hooks supporting Horns | Medium | Construction |  | Open | 2026-08-22 | Helen | 2026-08-22 | 30
DEF-0096 | 2026-08-20 |  | K1B-HS | Electrical | PIT-2171 |  | Installation | needs proper core marker | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0097 | 2026-08-20 |  | K1B-HS | Instrumentation | PIT-2171 |  | Installation | Loose T-Head | Medium | Construction |  | Open |  |  |  | 30
DEF-0098 | 2026-08-20 |  | K1B-HS | Instrumentation | PIT-2171 |  | Installation | Missing cable tag | Medium | Construction |  | Open |  |  |  | 30
DEF-0099 | 2026-08-20 |  | K1B-HS | Instrumentation | PIT-2171 |  | Installation | Spare cable entry is stripped | Medium | Construction |  | Open |  |  |  | 30
DEF-0100 | 2026-08-20 |  | K1B-HS | Electrical | TIT-1100 |  | Installation | Incomplete | Medium | Construction |  | Open |  |  |  | 30
DEF-0101 | 2026-08-20 |  | K1B-HS | Electrical | PIT-1202 |  | Installation | Incomplete | Medium | Construction |  | Open |  |  |  | 30
DEF-0102 | 2026-08-20 |  | K1B-HS | Electrical | PV-1200 |  | Installation | Incomplete | Medium | Construction |  | Open |  |  |  | 30
DEF-0103 | 2026-08-20 |  | K1B-HS | Electrical | PIT-1200 |  | Installation | Incomplete | Medium | Construction |  | Open |  |  |  | 30
DEF-0104 | 2026-08-20 |  | K1B-HS | Electrical | PIT-1201 |  | Installation | Incomplete | Medium | Construction |  | Open |  |  |  | 30
DEF-0105 | 2026-08-20 |  | K1B-HS | Instrumentation | PV-1200 |  | Installation | install plug | Medium | Construction |  | Open |  |  |  | 30
DEF-0106 | 2026-08-20 |  | K1B-HS | Instrumentation | PV-1200 |  | Installation | Install additional support | Medium | Construction |  | Open |  |  |  | 30
DEF-0107 | 2026-08-20 | Multiple | K1B-HS | Electrical | PIT-1013 |  | Installation | No field side cable tag Field tray not bonded to main tray | Medium | Construction |  | Open |  |  |  | 30
DEF-0108 | 2026-08-20 | Multiple | K1B-HS | Electrical | KV-1013 |  | Installation | Device is loose on mount Field tray not bonded to main Serivce loops for both PIT-1013 & KV-1013 are 9" in diameter | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0109 | 2026-08-20 | Multiple | K1B-HS | Electrical | FY-1015 |  | Installation | Needs terminations and core markers Field tray not bonded to main | Medium | Construction |  | Open |  |  |  | 30
DEF-0110 | 2026-08-20 | Multiple | K1B-HS | Electrical | PIT-1023 |  | Installation | Field tray not bonded to system | Medium | Construction |  | Closed | 2026-08-22 | Helen |  | 2
DEF-0111 | 2026-08-20 | Multiple | K1B-HS | Electrical | KV1023 |  | Installation | Gland is loose at 90 degree fitting | Medium | Construction |  | Closed | 2026-08-22 | Helen |  | 2
DEF-0112 | 2026-08-20 | Multiple | K1B-HS | Electrical | FIT-1015 |  | Installation | Service loops need relocation | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0113 | 2026-08-20 | Multiple | K1B-HS | Electrical | FY-1015 |  | Installation | Service loops need relocation | Medium | Construction |  | Closed | 2026-08-22 | Helen | 2026-08-22 | 2
DEF-0114 | 2026-08-20 |  |  | Electrical | KV-1023 |  | Installation | Field Tray needs Grommet installed | Medium | Construction |  | Open |  |  |  | 30
DEF-0115 | 2026-08-20 |  |  | Electrical | FY-1015 |  | Installation | Field Tray needs Grommet installed | Medium | Construction |  | Open |  |  |  | 30
DEF-0116 | 2026-08-19 | 29103-WPM-102 | K1B-DCS-001 | Electrical | JJB-102 |  | Installation | Loose shield/ Shrink not shrunk | Medium | Construction |  | Closed | 2026-08-20 | Helen | 2026-08-20 | 1
DEF-0117 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | All JJB's |  | Installation | Cable connectors are 'loose' | Medium | Construction |  | Closed | 2026-08-20 | Helen |  | 1
DEF-0118 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | JJB-105 |  | Documentation | Updated/ redlines drawings | High | QA/QC |  | Open |  |  |  | 31
DEF-0119 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | All JJB's |  | Code / Standard | SHV5 Terminal block ID's | Medium | Construction |  | In Progress |  |  |  | 31
DEF-0120 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | JJB-105 |  | Installation | Panduit Covers is missing (Ordered) | Medium | Construction |  | In Progress |  |  |  | 31
DEF-0121 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | JJB-XXX |  | Installation | Trunk shield to Individual drains | Medium | Construction |  | In Progress |  |  |  | 31
DEF-0122 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | JJB-301 |  | Installation | Shield Jumpers | Medium | Construction |  | In Progress |  |  |  | 31
DEF-0123 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | JJB-302 |  | Installation | Shield Jumpers | Medium | Construction |  | In Progress |  |  |  | 31
DEF-0124 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | JJB-100 |  | Installation | Loose Drains/Ferrules | Medium | Construction |  | Closed | 2026-08-20 | Helen |  | 1
DEF-0125 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | JJB-100 |  | Installation | Missing cable | Medium | Construction |  | Open |  |  |  | 31
DEF-0126 | 2026-08-19 | A Mods | K1B-DCS-001 | Electrical | JJB-104 |  | Installation | Bottom latch on JB will not close due to connector | Low | Construction |  | Open |  |  |  | 31
DEF-0127 | 2026-08-22 | 29103-BDG-101 | K1B-IA | Electrical | PIT-2172 |  | Installation | Connector is loose at gland | Medium | Construction |  | Closed | 2026-08-22 | Helen |  | 0
DEF-0128 | 2026-08-22 | 29103-BDG-101 | K1B-IA | Electrical | PIT-2172 |  | Installation | Missing cable tag & Field Side | Medium | Construction |  | Closed | 2026-08-22 | Helen |  | 0
DEF-0129 | 2026-08-22 | 29103-BDG-101 | K1B-IA | Electrical | PIT-2172 |  | Installation | Requires 1/2" Plug | Medium | Construction |  | Closed | 2026-08-22 | Helen |  | 0
DEF-0130 | 2026-08-22 | 29103-BDG-101 | K1B-IA | Electrical | PIT-2172 |  | Installation | Incorrect core marker | Medium | Construction |  | Closed | 2026-08-22 | Helen |  | 0
DEF-0131 | 2026-08-26 | A Mods | K1B-PV | Electrical | PIT-1035 |  | Installation | Loose at coupling, adhesive on cable (please remove) | Low | Construction |  | In Progress |  |  |  | 24
DEF-0132 | 2026-08-26 | A Mods | K1B-PV | Electrical | TIT-1035 |  | Installation | Field support, lift from gland | Medium | Construction |  | In Progress |  |  |  | 24
DEF-0133 | 2026-08-26 | A Mods | K1B-PE | Electrical | FIT-1034 |  | Installation | No Cable tag present | Low | Construction |  | In Progress |  |  |  | 24
DEF-0134 | 2026-08-26 | A Mods | K1B-PV | Electrical | PIT-1038 |  | Installation | Service loop is doubled up; cable rides tray as it comes out | Low | Construction |  | In Progress |  |  |  | 24
DEF-0135 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1034 |  | Installation | Support lift from gland | Low | Construction | [5 empty] | 24
DEF-0136 | 2026-08-26 | A Mods | K1B-PE | Electrical | PIT-1034 |  | Installation | Loose out coupling; support lift from the gland | Low | Construction | [5 empty] | 24
DEF-0137 | 2026-08-26 | A Mods | K1B-PE | Electrical | XY-1032 |  | Installation | Remove adhesive + grime from cable | Low | Construction | [5 empty] | 24
DEF-0138 | 2026-08-26 | A Mods | K1B-IA | Electrical | PIT-2072 |  | Installation | Missing cable tag; loose at coupling | Low | Construction | [5 empty] | 24
DEF-0139 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1014 |  | Installation | Support lift from gland; tidy up service loop + loose instrument | Low | Construction | [5 empty] | 24
DEF-0140 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1020J |  | Installation | No cable tag; field run tray bonding needed | Low | Construction | [5 empty] | 24
DEF-0141 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1020A |  | Installation | Armour is showing at connected conductor, field run tray needs bonding | Low | Construction | [5 empty] | 24
DEF-0142 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1010J |  | Installation | Field run tray needs bonding + grummet | High | Construction | [5 empty] | 24
DEF-0143 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1010A |  | Installation | Field run tray needs bonding/remove adhesive from cable | High | Construction | [5 empty] | 24
DEF-0144 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1014 |  | Installation | Needs support lift from gland; service loop needed, rubber gasket in connector is visible (reset connector) | Medium | Construction | [5 empty] | 24
DEF-0145 | 2026-08-26 | A Mods | K1B-PE | Electrical | PIT-1024 |  | Installation | Support lift from the gland | Low | Construction | [5 empty] | 24
DEF-0146 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1024 |  | Installation | Support lift from the gland | Low | Construction | [5 empty] | 24
DEF-0147 | 2026-08-26 | A Mods | K1B-PE | Electrical | PSHH-1029 |  | Installation | Tray bonding needs glyptal | Low | Construction | [5 empty] | 24
DEF-0148 | 2026-08-26 | A Mods | K1B-PV | Electrical | PIT-1028 |  | Installation | Loose connector, support lift from gland | Low | Construction | [5 empty] | 24
DEF-0149 | 2026-08-26 | A Mods | K1B-PV | Electrical | PIT-1025 |  | Installation | Loose coupler at the gland | Low | Construction | [5 empty] | 24
DEF-0150 | 2026-08-26 | A Mods | K1B-PV | Electrical | TIT-1025 |  | Installation | Instrument lid threads have a ding in it (hard to close) needs support lift from gland | Low | Construction | [5 empty] | 24
DEF-0151 | 2026-08-26 | A Mods | K1B-HS | Electrical | PIT-1021 |  | Installation | Cable routing into gland has to form below. (water flow) | Low | Construction | [5 empty] | 24
DEF-0152 | 2026-08-26 | A Mods | K1B-PE | Electrical | PY-1024 |  | Installation | Connector fitting is close to I-tubing + cable is touching tubing | Low | Construction | [5 empty] | 24
DEF-0153 | 2026-08-26 | A Mods | K1B-PE | Electrical | FIT-1024 |  | Installation | Remove point from cable | Low | Construction | [5 empty] | 24
DEF-0154 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1030A |  | Installation | Field run tray needs bonding; cable tag missing | Low | Construction | [5 empty] | 24
DEF-0155 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1030J |  | Installation | Field run tray needs bonding; missing cable tag | Medium | Construction | [5 empty] | 24
DEF-0156 | 2026-08-26 | A Mods | K1B-PE | Electrical | TIT-1020J |  | Installation | No cable tag; field run tray bonding needed. | Medium | Construction | [5 empty] | 24
DEF-0157 | 2026-09-05 | 29151 Drain Area |  | Electrical | 29203-ET-PE5002-1 |  | Code / Standard | Additional Tape required to secure 29203 ET PE5002-1 to pipe and remove slack. | Medium | Construction |  | Closed | 2026-09-05 | Levy Ostrup | 2026-09-05 | 0
DEF-0158 | 2026-09-05 | 29152 Drain Area |  | Electrical | 29151-65E-001-01 |  | Housekeeping | Cables 29151PP001-P & 29151DS001-P missing cable tag, + strap down to tray needed. -Need to clean inside of disconect | Medium | Construction |  | Closed | 2026-09-05 | Levy Ostrup | 2026-09-05 | 0
DEF-0159 | 2026-09-05 | 29153 Drain Area |  | Electrical | 29203-ET-PE5002-1PWK |  | Installation | Tighten connector to power box kit. Tighten lockrings to kit box. Core tags/ Cable tags missing. | Medium | Construction |  | Closed | 2026-09-05 | Levy Ostrup | 2026-09-05 | 0
DEF-0160 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-PIT-1027 |  | Installation | Panel JJB 102: missing cable tags | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0161 | 2026-09-06 | Multiple | Multiple | Electrical | JJB 101 |  | Installation | Nylar too long | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0162 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-KV-1017 |  | Installation | loose device, need to seal cable into connector | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0163 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-PIT-1017 |  | Installation | missing cable tags | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0164 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-PIT-1067 |  | Installation | Loose connector, grommet needed | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0165 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-PIT-1077 |  | Installation | Tighten connector, tighten 90 degree coupling. | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0166 | 2026-09-06 | Multiple | Multiple | Electrical | JJB 107 |  | Installation | Missing cable tags | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0167 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-KV-1067 |  | Installation | loose device | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0168 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-PIT-1057 |  | Installation | loose connector, grommet needed for I-Tray | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0169 | 2026-09-06 | Multiple | Multiple | Electrical | JJB 106 |  | Installation | Cable tags missing, install panduit | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0170 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-KV-1057 |  | Installation | re-seal connector / loose device | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0171 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-KV-1047 |  | Installation | loose connector, re-seal connector (re-gland) | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0172 | 2026-09-06 |  | Multiple | Electrical | JJB 104 |  | Installation | missing cabe tags, connector obstructing locking mechanism | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0173 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-KV-1037 |  | Installation | loose connector, re-gland, fix service loop, need ground 0h perpendicular to ladder tray. | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0174 | 2026-09-06 | Multiple | Multiple | Electrical | JJB 103 |  | Installation | missing cable tags | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0175 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-KV-1027 |  | Installation | loose device | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0176 | 2026-09-06 | R Mods | K1B-NG | Electrical | 29103-KV-1077 |  | Installation | re-gland connector / proper seal, tray not bonded, loose device, device needs to be aligned (Centered) | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0177 | 2026-09-06 | Mainline Separator | K1B-HS | Electrical | 29103-PIT-0900 |  | Installation | Missing cable tags, ground field tray | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0178 | 2026-09-06 | Mainline Separator | K1B-PE | Electrical | 29103-PIT-0916 |  | Installation | Tighten connector at 90 , missing cable tags | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0179 | 2026-09-06 | Mainline Separator | K1B-PE | Electrical | 29103-TIT-0916 |  | Installation | Loose connector, missing cable tags | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0180 | 2026-09-06 | Mainline Separator | K1B-PE | Electrical | 29103-FIT-0916 |  | Installation | Device needs to be tightened on base. Missing grommet and cable tags, seal better with connector/gland needs proper seal. Finish glyptal with band. | Medium | Construction |  | In Progress |  | Levy Ostrup |  | 13
DEF-0181 | 2026-09-07 | Mainline Cooler |  | Electrical | 29103-A-001-UHE-1 |  | Damage | Mainline cooler, shrink is torn off conductors | Medium | Construction |  | Closed | 2026-09-07 | Levy Ostrup | 2026-09-07 | 0
DEF-0182 | 2026-09-07 | Mainline Cooler |  | Electrical | 29103-A-001-UHE-2 |  | Damage | Shrink is also torn a little bit. Set screw on 29103-A-001-UHE-2 Bucket A phase was stripped | Medium | Construction |  | Closed | 2026-09-07 | Levy Ostrup | 2026-09-07 | 0
DEF-0183 | 2026-09-07 | Mainline Cooler |  | Electrical | 29103-A-001-UHE-3 |  | Damage | Screw looks cross threaded, didn’t want to touch it | Medium | Construction |  | Closed | 2026-09-07 | Levy Ostrup | 2026-09-07 | 0
DEF-0184 | 2026-09-07 | Mainline Cooler |  | Electrical | 29103-A-001-UHE-4 |  | Damage | scratched up a little, but probably okay | Medium | Construction |  | Closed | 2026-09-07 | Levy Ostrup | 2026-09-07 | 0
DEF-0185 | 2026-09-07 | Mainline Cooler |  | Electrical | 29103-A-001-UHE-5 |  | Damage | There was another screw that looked cross threaded. But was abel to be fixed | Medium | Construction |  | Closed | 2026-09-07 | Levy Ostrup | 2026-09-07 | 0
DEF-0186 | 2026-09-05 | Multiple | Multiple | Electrical | FY-0913 |  | Installation | Connector Loose; shrink in JJB for shield are short | Medium | Construction |  | Closed | 2026-09-05 | Levy Ostrup | 2026-09-08 | 0
DEF-0187 | 2026-09-05 | Multiple | Multiple | Electrical | FIT-0913A |  | Installation | Device is loose | Medium | Construction | [5 empty] | 14
DEF-0188 | 2026-09-05 | Multiple | Multiple | Electrical | LIT-0920 |  | Installation | Threads on device need lubrication | Medium | Construction | [5 empty] | 14
DEF-0189 | 2026-09-05 | Multiple | Multiple | Electrical | TIT-0921 |  | Installation | Device & connector need to be tightened | Medium | Construction | [5 empty] | 14
DEF-0190 | 2026-09-05 | Multiple | Multiple | Electrical | PIT-0908 |  | Installation | PIT located on PG loctation; Helen to confirm? | Medium | Construction | [5 empty] | 14
DEF-0191 | 2026-09-05 | Multiple | Multiple | Electrical | PIT-0909 |  | Installation | PIT located on PG loctation; Helen to confirm? | Medium | Construction | [5 empty] | 14
DEF-0192 | 2026-09-05 | Multiple | Multiple | Electrical | PIT-0920 |  | Installation | Set screw loose | Medium | Construction |  | Closed | 2026-09-05 | Levy Ostrup | 2026-09-08 | 0
DEF-0193 | 2026-09-05 | Multiple | Multiple | Electrical | PIT-0921 |  | Installation | Set screw loose | Medium | Construction |  | Closed | 2026-09-05 | Levy Ostrup | 2026-09-08 | 0
DEF-0194 | 2026-09-05 | Multiple | Multiple | Electrical | PIT-0923 |  | Installation | Set screw loose | Medium | Construction |  | Closed | 2026-09-05 | Levy Ostrup | 2026-09-08 | 0
DEF-0195 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-LIT-0203 |  | Installation | Ensure all field run tray up top is bonded to system and has glyptal installed. Coil drain under boot. Loose instrument: needs to be tightened. No cable tags. Install grommet on field run tray. | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0196 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29203-LIT-0221 |  | Installation | Install capillary support. Install field tray run bond and grommet + glyptal. Install service loop 10" in diameter. Cable tag missing. Loose gland at coupling. New clean undamaged core markers. | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0197 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-XY-0204 |  | Installation | No cable tags. Drain needs to be coiled under boot. | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0198 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-PIT-0205 |  | Installation | No cable tags. Service loops are 6" in diamater. Tyrap cable into tray. Rubber grommet protruding at connector. Field run tray requires more support. | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0199 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29203-XY-0220 |  | Installation | Drain needs to be coiled under boot. No cable tags | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0200 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-XY-0201 |  | Installation | Drain needs to be coiled under boot. No cable tags | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0201 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-XY-0202 |  | Installation | Drain needs to be coiled under boot. No cable tags | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0202 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-PIT-0205 |  | Installation | Drain needs to be coiled under boot. No cable tags. Grommet needed for field tray run. | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0203 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-XY-0203 |  | Installation | Drain needs to be coiled under boot. No cable tags. Core marker is incorrect. Service loop no igger than 6" in diameter | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0204 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-LIT-0205 |  | Installation | Drain needs to be coiled under boot. No cable tags. Orange lead is damaged; Re-term required. Replace damaged/worn core markers | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0205 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-HTP-001 |  | Installation | System ground needs sealing ring and plastic bushing. Missing cable tags. Panel unfinished, panduit open, open unglanded connectors waiting power cables. Support 1 ft from the gland; tyrap into tray. Vacuum | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0206 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-DCSFF-JB-001 |  | Installation | Cabinet sits loose on the mount / Should have used square washers - In turn small hair line cracks are showing both top corners. Remove adhesive on front door. Support 1' from the gland. No cable tags. Vacuum out cabinet. Loose LB. Ferroles are crimped incorrectly; shields are poorly shrunk and exposed. In some broken wires, install boots at the end of the mylar. Taps in gutter need insulation tape + rubber tape. Clean up sloppy glyptal. | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0207 | 2026-09-11 | Drain Tank 2 | Multiple | Electrical | 29152-PT-001 |  | Installation | Double nut day hooks and cut ends. Up size XO lug and land neutral. Secondaries are short and reaching; why no sway or even hard 90? Primaries rest on other phase lugs; requires 1" of seperation. Tighten the GRL on LB. Vacuum cabinet. Tyrap main feed into tray. Red phase is score w/ knife | Medium | Construction |  |  |  | Levy Ostrup |  | 8
DEF-0208 | 2026-09-13 | South Drain Tank | Multiple | Electrical | 29203-LIT-0211 |  | Installation | Need core markers and cable tags. Coil shield under boot. Install grommet on all sides of FRT; needs a longer run of FRT. | Medium | Construction |  | Open |  |  |  | 6
DEF-0209 | 2026-09-13 | South Drain Tank | Multiple | Electrical | 29203-LIT-0210 |  | Installation | Need tubing supports; tighten device supports. Need grommet on FRT; reduce service loop to 6" max diameter. Coil shield under boot. Need tubing supports; tighten device supports. | Medium | Construction |  | Open |  |  |  | 6
DEF-0210 | 2026-09-14 | South Drain Tank | Multiple | Electrical | 29203-XV-0210 |  | Installation | Need cable tags on both ends. | Medium | Construction |  | Open |  |  |  | 5
DEF-0211 | 2026-09-14 | South Drain Tank | Multiple | Electrical | 29151-XV-0101 |  | Installation | Need cable tags on both ends. Need glyptal for grounding points on FRT. | Medium | Construction |  | Open |  |  |  | 5
DEF-0212 | 2026-09-14 | South Drain Tank | Multiple | Electrical | 29151-XV-0102 |  | Installation | Need cable tags on both ends. Incorrect field wiring. | Medium | Construction |  | In Progress |  |  |  | 5 |  |  | Incorrect field wiring corrected 09/14/2026 ). Cable tags on both ends still outstanding.
DEF-0213 | 2026-09-14 | South Drain Tank | Multiple | Electrical | 29151-PIT-0105 |  | Installation | Need cable tags on both ends. | Medium | Construction |  | Open |  |  |  | 5
DEF-0214 | 2026-09-14 | South Drain Tank | Multiple | Electrical | 29151-LIT-0103 |  | Installation | Need cable tags on both ends; install 6" max diameter service loop. Need grommet for FRT. | Medium | Construction |  | Open |  |  |  | 5
DEF-0215 | 2026-09-14 | South Drain Tank | Multiple | Electrical | 29151-LIT-0105 |  | Installation | Need cable tags on both ends. Need core markers on field device. | Medium | Construction |  | Open |  |  |  | 5
DEF-0216 | 2026-09-14 | South Drain Tank | Multiple | Electrical | 29151-XV-0104 |  | Installation | Need cable tags on both ends. Coil shield under boot. | Medium | Construction |  | Open |  |  |  | 5
DEF-0217 | 2026-09-14 | South Drain Tank | Multiple | Electrical | 29151-PSE-0106 |  | Installation | Need cable tags on both ends. Coil shield under boot. Reduce service loop to 6" diameter max. Incorrect connector size for cable. | Medium | Construction |  | Open |  |  |  | 5
DEF-0218 | 2026-09-13 | South Drain Tank | Multiple | Electrical | 29203-TW-0101 |  | Installation | Need cable tags for both ends; need 1 core marker for red lead and all core markers for RTD. | Medium | Construction |  | Open |  |  |  | 6
DEF-0219 | 2026-09-13 | South Drain Tank | Multiple | Electrical | 29203-TIT-0101 |  | Installation | Coil shield under boot. Need cable tags for both ends; need new/clean core marker. | Medium | Construction |  | Open |  |  |  | 6
DEF-0220 | 2026-09-15 | CMM / Main line | Multiple | Electrical | 29103-PIT-1600 |  | Installation | Need to update core markers. | Medium | Construction |  | Closed | 2026-09-15 | Levy Ostrup | 2026-09-15
DEF-0221 | 2026-09-15 | CMM / Main line | Multiple | Electrical | 29103-PIT-1600 |  | Installation | Need to cut FRT to shorter length. | Medium | Construction |  | Closed | 2026-09-15 | Levy Ostrup | 2026-09-15
DEF-0222 | 2026-09-15 | CMM / Main line | Multiple | Electrical | 29103-PV-1400 |  | Installation | Need to gland and terminate device. | Medium | Construction |  | Closed | 2026-09-15 | Levy Ostrup | 2026-09-15
DEF-0223 | 2026-09-13 | South Drain Tank | Multiple | Electrical | 29103-TIT-0015P |  | Documentation | Tag on device does not match any prints. | Medium | Construction |  | Open
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | TANK1-1-PWK | YCQE-PS-048 (2026-09-27) | Installation | Needs tray grommet where cable exits tray. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Punchlist category C. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | ETHC-4102-PWK | YCQE-PS-048 (2026-09-27) | Installation | Missing GRL on power cable. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | ETFG-4102-PWK | YCQE-PS-048 (2026-09-27) | Installation | Needs tray grommet where cable exits tray. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | ETDR-4100-PWK | YCQE-PS-048 (2026-09-27) | Installation | Incorrect heat trace installed; should be 43 W/m HT. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | ETHC-5008-PWK | YCQE-PS-048 (2026-09-27) | Installation | Incorrect cable installed; should be #6 AWG. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | ETPE-5002-PWK / ETPE-5002-2-R1 | YCQE-PS-048 (2026-09-27) | Installation | Incorrect location of RTD according to ISO. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | TANK1-5-PWK | YCQE-PS-048 (2026-09-27) | Installation | Missing HT termination kit. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | ETMT-0002-PWK | YCQE-PS-048 (2026-09-27) | Installation | Missing GRL on PWK-3; PWK under vessel needs support. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | ETPG-4100-PWK | YCQE-PS-048 (2026-09-27) | Installation | Missing GRL on power cable. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-27 | Drain Tank 1 | Multiple | Electrical | TANK1-3-R-1 | YCQE-PS-048 (2026-09-27) | Installation | Boot too short in device. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Tag as written on punchlist.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-PE1102-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29); YCQE-E&I-113 | Installation | No core markers / cable tags; not terminated; no GRL on HT connector. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Combined: punchlist item + small power ITR remarks.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-PE1201-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29); YCQE-E&I-113 | Installation | Cable tag upside down. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Combined: punchlist item + small power ITR remarks.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-P1204-2-PWK-1 | YCQE-PS-048 Internal (2026-09-29); YCQE-E&I-113 | Installation | Missing cable tag; check service loop on HT cold lead. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Combined: punchlist item + small power ITR remarks.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-PG1201-2-PWK-1 | YCQE-PS-048 Internal (2026-09-29) | Installation | Missing power kit. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-PE1802-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29); YCQE-E&I-113 | Installation | Needs core markers; cable tag upside down. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Combined: punchlist item + small power ITR remarks.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-ST1103-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29) | Installation | No power cable. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-FG1203-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29) | Installation | Needs cable tag on device side. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-PG1101-2-PWK-1 | YCQE-PS-048 Internal (2026-09-29) | Installation | Cable pulled; not glanded / terminated. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-FG1105-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29) | Installation | Needs device tag at ambient box. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-PE1101-2-PWK-1 | YCQE-PS-048 Internal (2026-09-29) | Installation | Not terminated. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-PE1101-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29) | Installation | Not terminated. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Note: small power ITR for this cable (Sept 28) shows all items initialed with no remarks - verify.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-P1201-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29); YCQE-E&I-113 | Installation | Core markers missing; not terminated. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Combined: punchlist item + small power ITR remarks.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-ST1001-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29) | Installation | MI needs glanding; no power cable. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-P1104-2-PWK-1 | YCQE-PS-048 Internal (2026-09-29); YCQE-E&I-113 | Installation | Missing cable tags both sides. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Combined with small power ITR written as 29103-ET-PE1104-2-PWK-1 (same remark) - confirm P vs PE tag.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-PG1101-1-PWK-1 | YCQE-PS-048 Internal (2026-09-29); YCQE-E&I-113 | Installation | Missing core markers on power cable. | Medium | Construction |  | Open | [6 empty] | Punched by Murtesa / Liam. Combined: punchlist item + small power ITR remarks.
| 2026-09-29 | 29103-WPM-101/102 | K1B-600V-EHT | Electrical | 29103-ET-P1101-1-PWK-1 | YCQE-E&I-113 | Installation | Cable is pulled and glanded; not terminated. | Medium | Construction |  | Open | [6 empty] | From small power ITR remarks (Sept 29); not on punchlist.
Formulas:
Days Open = IF([Date Identified]="","",MAX(0,IF([Status]="Closed",IF([Date Corrected]="",TODAY()-[Date Identified],[Date Corrected]-[Date Identified]),TODAY()-[Date Identified])))
Overdue? = IF(OR([Deficiency Description]="",[Target Date]="",[Status]="Closed"),"",IF(TODAY()>[Target Date],"Yes","No"))
Overdue? = IF(OR([Deficiency Description]="",#REF!="",[Status]="Closed"),"",IF(TODAY()>#REF!,"Yes","No"))
Note on I6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Enter a clear, objective description of the observed deficiency and the required correction.
Note on M6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Ready for Verification after construction reports the correction complete; QA/QC should move it to Closed after verification.

## Dashboard
DEFICIENCY STATUS DASHBOARD
Status | Count | Priority | Open Count | Key Metric | Value
Open | 116 | Critical | 1 | Total Logged | 223
In Progress | 33 | High | 7 | Currently Overdue | 6
Ready for Verification | 0 | Medium | 113 | Average Days Open | 30.9726
Closed | 34 | Low | 68
Dashboard figures update automatically from the Deficiency Tracker. Use the main log for detailed review, filtering, verification, and close-out records.

## Lists
Status | Priority | Discipline | Category | Responsible Party | Area / Module | System
Open | Critical | Electrical | Installation | Construction | 29103-BDG-101 | Multiple
In Progress | High | Instrumentation | Damage | QA/QC | 29103-ELM-101 | K1B-600V-UPS
Ready for Verification | Medium | Mechanical | Documentation | Engineering | 29103-EQM-101 | K1B-600V
Closed | Low | Civil | Testing | Vendor | 29209-EQM-103 | K1B-600V-ESP
On Hold |  | Structural | Accessibility | Client | 29103-EQM-102/103 | K1B-600V-SUS
Rejected |  | Insulation | Code / Standard | Subcontractor | 29209-EQM-101/102 | K1B-F&G
|  | Coatings | Housekeeping | Other | 29103-PRM-101 | K1B-HS
|  | Other | Other |  | 29103-CMM-101 | K1B-NG
[5 empty] | 29103-PRM-201 | K1B-PV
[5 empty] | 29103-CMM-201 | K1B-PE
[5 empty] | 29103-WPM-101 | DT-29151
[5 empty] | 29103-WPM-102 | DT-29152
[5 empty] | 29103-WPM-103 | K1B-600V-EHT
[5 empty] | 29103-WPM-104 | K1B-Ehouse
[5 empty] | 29103-A-1P/2P | K2B-600V-EGEN
[5 empty] | 29103-A-1S/2S | K1B-DCS-001
[5 empty] | 29103-A-3P/4P | K1B-600V-AHU
[5 empty] | 29103-A-3S/4S | K1B-DCS-001
[5 empty] | 29103-A-5P/6P | K1B-IA
29103-A-5S/6S
Multiple
A Mods
R Mods
Add project-specific Areas / Modules and Systems in columns F and G. Dropdowns in the tracker will update automatically within the reserved list range.