## Summary
EHT ITR Summary
Panel | Total | Traces | Power | RTDs | RTD Cables | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete
29103-HTP-102 | 144 | 56 | 38 | 22 | 28 | 144 / 144 | 0 / 144 | 10 / 56 | 0 / 56 | 0 / 56 | 0 / 38 | 0 / 66 | 0 / 22 | 0 / 22 | 0 / 144 | 0 / 144
29103-HTP-100 | 60 | 21 | 15 | 12 | 12 | 60 / 60 | 2 / 60 | 2 / 21 | 2 / 21 | 0 / 21 | 0 / 15 | 0 / 27 | 0 / 12 | 0 / 12 | 4 / 60 | 0 / 60
29103-HTP-101 | 75 | 28 | 19 | 13 | 15 | 75 / 75 | 0 / 75 | 8 / 28 | 2 / 28 | 0 / 28 | 0 / 19 | 0 / 34 | 0 / 13 | 0 / 13 | 4 / 75 | 0 / 75
29103-HTP-004 | 262 | 116 | 48 | 47 | 51 | 262 / 262 | 0 / 262 | 45 / 116 | 0 / 116 | 0 / 116 | 0 / 48 | 0 / 99 | 0 / 47 | 0 / 47 | 0 / 262 | 0 / 262
29103-HTP-005 | 248 | 108 | 47 | 45 | 48 | 248 / 248 | 0 / 248 | 28 / 108 | 0 / 108 | 0 / 108 | 0 / 47 | 0 / 95 | 0 / 45 | 0 / 45 | 0 / 248 | 0 / 248
29103-HTP-003 | 269 | 118 | 49 | 49 | 53 | 269 / 269 | 9 / 269 | 32 / 118 | 3 / 118 | 0 / 118 | 0 / 49 | 0 / 102 | 0 / 49 | 0 / 49 | 9 / 269 | 0 / 269
29103-HTP-002 | 242 | 106 | 46 | 44 | 46 | 242 / 242 | 59 / 242 | 19 / 106 | 3 / 106 | 0 / 106 | 10 / 46 | 33 / 92 | 1 / 44 | 23 / 44 | 62 / 242 | 33 / 242
29151-HTP-001 | 35 | 18 | 17 | 0 | 0 | 35 / 35 | 17 / 35 | 1 / 18 | 0 / 18 | 0 / 18 | 17 / 17 | 17 / 17 | 0 / 0 | 0 / 0 | 17 / 35 | 17 / 35
29152-HTP-001 | 33 | 16 | 17 | 0 | 0 | 33 / 33 | 17 / 33 | 0 / 16 | 0 / 16 | 0 / 16 | 17 / 17 | 17 / 17 | 0 / 0 | 0 / 0 | 0 / 33 | 0 / 33
Drain Tank Fieldbus | 9 | 0 | 0 | 0 | 0 | 9 / 9 | 9 / 9 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 9 / 9 | 0 / 0 | 0 / 0 | 9 / 9 | 9 / 9
Total | 1377 | 587 | 296 | 232 | 253

## 29103-HTP-102
29103-HTP-102
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29103-ET-A001-1-1 | 29103-ET-A001-1 | HTC-31 / CB-31 | 29103-A-001 | 29103-65R-ET-A001-01-01 | 13.1 | 29103-ET-A001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 5.2 m m | Levy Ostrup
EHT Trace | 29103-ET-A001-1-2 | 29103-ET-A001-1 | HTC-31 / CB-31 | 29103-A-001 | 29103-65R-ET-A001-01-01 | 13.1 | 29103-ET-A001-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 5.2 m m | Levy Ostrup
EHT Trace | 29103-ET-HC1901-1-1 | 29103-ET-HC1901-1 | HTC-05 / CB-05 | 29103-HC-1901 | 29103-65R-ET-HC1901-01-01 | 13.1 | 29103-ET-HC1901-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20HTV2-CT | 12.1 m m | Levy Ostrup
EHT Trace | 29103-ET-HC1902-1-1 | 29103-ET-HC1902-1 | 29103-AMB-015 | 29103-HC-1902 | 29103-65R-ET-HC1902-01-01 | 13.1 | 29103-ET-HC1902-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 17 m m | Levy Ostrup
EHT Trace | 29103-ET-HC1903-1-1 | 29103-ET-HC1903-1 | HTC-04 / CB-04 | 29103-HC-1903, 29103-HC-1902 | 29103-65R-ET-HC1903-01-01 | 13.1 | 29103-ET-HC1903-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 28.7 m m | Levy Ostrup
EHT Trace | 29103-ET-HC1903-1-2 | 29103-ET-HC1903-1 | HTC-04 / CB-04 | 29103-HC-1904 | 29103-65R-ET-HC1903-01-01 | 13.1 | 29103-ET-HC1903-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 32 m m | Levy Ostrup
EHT Trace | 29103-ET-HC1905-1-1 | 29103-ET-HC1905-1 | 29103-AMB-015 | 29103-HC-1910, 29103-HC-1905 | 29103-65R-ET-HC1905-01-01 | 13.1 | 29103-ET-HC1905-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 55.5 m m | Levy Ostrup
EHT Trace | 29103-ET-HC1906-1-1 | 29103-ET-HC1906-1 | HTC-06 / CB-06 | 29103-HC-1906, 29103-HC-1902 | 29103-65R-ET-HC1906-01-01 | 13.1 | 29103-ET-HC1906-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 29.9 m m | Levy Ostrup
EHT Trace | 29103-ET-HC1906-1-2 | 29103-ET-HC1906-1 | HTC-06 / CB-06 | 29103-HC-1907 | 29103-65R-ET-HC1906-01-01 | 13.1 | 29103-ET-HC1906-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 31.5 m m | Levy Ostrup
EHT Trace | 29103-ET-HC1909-1-1 | 29103-ET-HC1909-1 | 29103-AMB-015 | 29103-HC-1909, 29103-HC-1908 | 29103-65R-ET-HC1909-01-01 | 13.1 | 29103-ET-HC1909-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 49 m m | Levy Ostrup
EHT Trace | 29103-ET-MT0001-1-1 | 29103-ET-MT0001-1 | HTC-09 / CB-09 | 29103-MT-0001 | 29103-65R-ET-MT0001-01-01 | 13.1 | 29103-ET-MT0001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20HTV2-CT | 3.7 m m | Levy Ostrup
EHT Trace | 29103-ET-MT0001-1-2 | 29103-ET-MT0001-1 | HTC-09 / CB-09 | 29103-MT-0001 | 29103-65R-ET-MT0001-01-01 | 13.1 | 29103-ET-MT0001-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20HTV2-CT | 12.3 m m | Levy Ostrup
EHT Trace | 29103-ET-P001A-1-1 | 29103-ET-P001A-1 | HTC-02 / CB-02 | 29103-P-001A | 29103-65R-ET-P001A-01-01 | 13.1 | 29103-ET-P001A-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 15HTV2-CT | 8.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P001A-2-1 | 29103-ET-P001A-2 | HTC-07 / CB-07 | 29103-P-001A | 29103-65R-ET-P001A-02-01 | 13.1 | 29103-ET-P001A-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-P001A-3-1 | 29103-ET-P001A-3 | HTC-08 / CB-08 | 29103-P-001A | 29103-65R-ET-P001A-03-01 | 13.1 | 29103-ET-P001A-3-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10XTVR2-CT | 27 m m | Levy Ostrup
EHT Trace | 29103-ET-P001A-3-2 | 29103-ET-P001A-3 | HTC-08 / CB-08 | 29103-P-001A | 29103-65R-ET-P001A-03-01 | 13.1 | 29103-ET-P001A-3-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-P001A-4-1 | 29103-ET-P001A-4 | HTC-13 / CB-13 | 29103-P-001A | 29103-65R-ET-P001A-04-01 | 13.1 | 29103-ET-P001A-4-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10XTVR2-CT | 27 m m | Levy Ostrup
EHT Trace | 29103-ET-P001A-4-2 | 29103-ET-P001A-4 | HTC-13 / CB-13 | 29103-P-001A | 29103-65R-ET-P001A-04-01 | 13.1 | 29103-ET-P001A-4-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10XTVR2-CT | 24.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P001B-1-1 | 29103-ET-P001B-1 | HTC-10 / CB-10 | 29103-P-001B | 29103-65R-ET-P001B-01-01 | 13.1 | 29103-ET-P001B-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 15HTV2-CT | 8.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P001B-2-1 | 29103-ET-P001B-2 | HTC-15 / CB-15 | 29103-P-001B | 29103-65R-ET-P001B-02-01 | 13.1 | 29103-ET-P001B-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-P001B-3-1 | 29103-ET-P001B-3 | HTC-11 / CB-11 | 29103-P-001B | 29103-65R-ET-P001B-03-01 | 13.1 | 29103-ET-P001B-3-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10XTVR2-CT | 27 m m | Levy Ostrup
EHT Trace | 29103-ET-P001B-3-2 | 29103-ET-P001B-3 | HTC-11 / CB-11 | 29103-P-001B | 29103-65R-ET-P001B-03-01 | 13.1 | 29103-ET-P001B-3-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-P001B-4-1 | 29103-ET-P001B-4 | HTC-16 / CB-16 | 29103-P-001B | 29103-65R-ET-P001B-04-01 | 13.1 | 29103-ET-P001B-4-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10XTVR2-CT | 27 m m | Levy Ostrup
EHT Trace | 29103-ET-P001B-4-2 | 29103-ET-P001B-4 | HTC-16 / CB-16 | 29103-P-001B | 29103-65R-ET-P001B-04-01 | 13.1 | 29103-ET-P001B-4-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10XTVR2-CT | 24.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P1003-1-1 | 29103-ET-P1003-1 | HTC-19 / CB-19 | 29103-P-1003 | 29103-65R-ET-P1003-01-01 | 13.1 | 29103-ET-P1003-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 38.1 Ω | 2026-05-17 | [12 empty] | D/32SQ3374/30.1M/1899/277/2.1M/LS23A/X/N12 | 30.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1003-1-2 | 29103-ET-P1003-1 | HTC-19 / CB-19 | 29103-P-1003 | 29103-65R-ET-P1003-01-01 | 13.1 | 29103-ET-P1003-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 38.1 Ω | 2026-05-17 | [12 empty] | D/32SQ3374/30.1M/1899/277/2.1M/LS23A/X/N12 | 30.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1004-1-1 | 29103-ET-P1004-1 | HTC-20 / CB-20 | 29103-P-1004 | 29103-65R-ET-P1004-01-01 | 13.1 | 29103-ET-P1004-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 30.3 Ω | 2026-05-17 | [12 empty] | D/32SQ3200/44.1M/2426/277/2.1M/LS23A/X/N12 | 44.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1004-1-2 | 29103-ET-P1004-1 | HTC-20 / CB-20 | 29103-P-1004 | 29103-65R-ET-P1004-01-01 | 13.1 | 29103-ET-P1004-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 30.2 Ω | 2026-05-17 | [12 empty] | D/32SQ3200/44.1M/2426/277/2.1M/LS23A/X/N12 | 44.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1920-1-1 | 29103-ET-P1920-1 | HTC-22 / CB-22 | 29103-P-1920 | 29103-65R-ET-P1920-01-01 | 13.1 | 29103-ET-P1920-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 117.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P1920-2-1 | 29103-ET-P1920-2 | 29103-AMB-016 | 29103-P-1920 | 29103-65R-ET-P1920-02-01 | 13.1 | 29103-ET-P1920-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 32.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1901-1-1 | 29103-ET-PG1901-1 | 29103-AMB-016 | 29103-PG-1902, 29103-PG-1901 | 29103-65R-ET-PG1901-01-01 | 13.1 | 29103-ET-PG1901-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 16.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1903-1-1 | 29103-ET-PG1903-1 | HTC-12 / CB-12 | 29103-PG-1903 | 29103-65R-ET-PG1903-01-01 | 13.1 | 29103-ET-PG1903-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10HTV2-CT | 54.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST0001-1-1 | 29103-ET-ST0001-1 | HTC-14 / CB-14 | 29103-ST-0001 | 29103-65R-ET-ST0001-01-01 | 13.1 | 29103-ET-ST0001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2275/24.1M/352/277/1.2M/LS23A/X/N12 | 24.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST0003-1-1 | 29103-ET-ST0003-1 | 29103-AMB-016 | 29103-V-0001, 29103-ST-0003 | 29103-65R-ET-ST0003-01-01 | 13.1 | 29103-ET-ST0003-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 10.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1816-1-1 | 29103-ET-ST1816-1 | 29103-AMB-016 | 29103-ST-1817, 29103-ST-1816, 29103-ST-0002 | 29103-65R-ET-ST1816-01-01 | 13.1 | 29103-ET-ST1816-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 34.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1816-1-2 | 29103-ET-ST1816-1 | 29103-AMB-016 | 29103-ST-1818, 29103-ST-1816 | 29103-65R-ET-ST1816-01-01 | 13.1 | 29103-ET-ST1816-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 27.1 m m | Levy Ostrup
EHT Trace | 29103-ET-V1900-1-1 | 29103-ET-V1900-1 | HTC-17 / CB-17 | 29103-V-1900 | 29103-65R-ET-V1900-01-01 | 13.1 | 29103-ET-V1900-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20HTV2-CT | 17.1 m m | Levy Ostrup
EHT Trace | 29103-ET-V1900-1-2 | 29103-ET-V1900-1 | HTC-17 / CB-17 | 29103-V-1900 | 29103-65R-ET-V1900-01-01 | 13.1 | 29103-ET-V1900-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20HTV2-CT | 15.2 m m | Levy Ostrup
EHT Trace | 29209-ET-A001-1-1 | 29209-ET-A001-1 | HTC-29 / CB-29 | 29209-A-001 | 29209-65R-ET-A001-01-01 | 13.1 | 29209-ET-A001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 4.9 m m | Levy Ostrup
EHT Trace | 29209-ET-A001-1-2 | 29209-ET-A001-1 | HTC-29 / CB-29 | 29209-A-001 | 29209-65R-ET-A001-01-01 | 13.1 | 29209-ET-A001-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 4.9 m m | Levy Ostrup
EHT Trace | 29209-ET-A001-1-3 | 29209-ET-A001-1 | HTC-29 / CB-29 | 29209-A-001 | 29209-65R-ET-A001-01-01 | 13.1 | 29209-ET-A001-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV2-CT | 1.2 m m | Levy Ostrup
EHT Trace | 29209-ET-HC6010-1-1 | 29209-ET-HC6010-1 | HTC-25 / CB-25 | 29209-HC-6010 | 29209-65R-ET-HC6010-01-01 | 13.1 | 29209-ET-HC6010-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 27.8 m m | Levy Ostrup
EHT Trace | 29209-ET-HC6010-1-2 | 29209-ET-HC6010-1 | HTC-25 / CB-25 | 29209-HC-6010 | 29209-65R-ET-HC6010-01-01 | 13.1 | 29209-ET-HC6010-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV2-CT | 10.9 m m | Levy Ostrup
EHT Trace | 29209-ET-P6020-1-1 | 29209-ET-P6020-1 | HTC-23 / CB-23 | 29209-P-6020 | 29209-65R-ET-P6020-01-01 | 13.1 | 29209-ET-P6020-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/54.9M/1976/277/2.1M/LS23A/X/N12 | 54.9 m m | Levy Ostrup
EHT Trace | 29209-ET-P6020-1-2 | 29209-ET-P6020-1 | HTC-23 / CB-23 | 29209-P-6020 | 29209-65R-ET-P6020-01-01 | 13.1 | 29209-ET-P6020-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.6 Ω | 2026-05-17 | [12 empty] | E/32SQ3100/36.6M/1486/138/2.1M/LS23A/X/N12 | 36.6 m m | Levy Ostrup
EHT Trace | 29209-ET-P6020-1-3 | 29209-ET-P6020-1 | HTC-23 / CB-23 | 29209-P-6020 | 29209-65R-ET-P6020-01-01 | 13.1 | 29209-ET-P6020-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.6 Ω | 2026-05-17 | [12 empty] | D/32SQ3100/36.6M/1486/138/2.1M/LS23A/X/N12 | 36.6 m m | Levy Ostrup
EHT Trace | 29209-ET-P6021-1-1 | 29209-ET-P6021-1 | HTC-18 / CB-18 | 29209-P-6021 | 29209-65R-ET-P6021-01-01 | 13.1 | 29209-ET-P6021-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/54.9M/1976/277/2.1M/LS23A/X/N12 | 54.9 m m | Levy Ostrup
EHT Trace | 29209-ET-P6021-1-2 | 29209-ET-P6021-1 | HTC-18 / CB-18 | 29209-P-6021 | 29209-65R-ET-P6021-01-01 | 13.1 | 29209-ET-P6021-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3100/36.6M/1486/138/2.1M/LS23A/X/N12 | 36.6 m m | Levy Ostrup
EHT Trace | 29209-ET-P6021-1-3 | 29209-ET-P6021-1 | HTC-18 / CB-18 | 29209-P-6021 | 29209-65R-ET-P6021-01-01 | 13.1 | 29209-ET-P6021-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/36.6M/1486/138/2.1M/LS23A/X/N12 | 36.6 m m | Levy Ostrup
EHT Trace | 29209-ET-P6022-1-1 | 29209-ET-P6022-1 | HTC-21 / CB-21 | 29209-P-6022 | 29209-65R-ET-P6022-01-01 | 13.1 | 29209-ET-P6022-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3293/42.6M/1742/277/1.2M/LS23A/X/N12 | 42.6 m m | Levy Ostrup
EHT Trace | 29209-ET-P6022-1-2 | 29209-ET-P6022-1 | HTC-21 / CB-21 | 29209-P-6022 | 29209-65R-ET-P6022-01-01 | 13.1 | 29209-ET-P6022-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3100/38.2M/1429/138/1.2M/LS23A/X/N12 | 38.2 m m | Levy Ostrup
EHT Trace | 29209-ET-P6022-1-3 | 29209-ET-P6022-1 | HTC-21 / CB-21 | 29209-P-6022 | 29209-65R-ET-P6022-01-01 | 13.1 | 29209-ET-P6022-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/38.2M/1429/138/1.2M/LS23A/X/N12 | 38.2 m m | Levy Ostrup
EHT Trace | 29209-ET-PG6003-1-1 | 29209-ET-PG6003-1 | HTC-27 / CB-27 | 29209-PG-6003 | 29209-65R-ET-PG6003-01-01 | 13.1 | 29209-ET-PG6003-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 34.5 Ω | 2026-05-18 | [12 empty] | D/32SQ3200/50M/2160/277/2.1M/LS23A/X/N12 | 50 m m | Levy Ostrup
EHT Trace | 29209-ET-PG6003-1-2 | 29209-ET-PG6003-1 | HTC-27 / CB-27 | 29209-PG-6003 | 29209-65R-ET-PG6003-01-01 | 13.1 | 29209-ET-PG6003-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 82.7 Ω | 2026-05-18 | [12 empty] | D/32SB2114/21.2M/962/277/2.1M/LS23A/X/N12 | 21.2 m m | Levy Ostrup
EHT Trace | 29209-ET-ST6005-1-1 | 29209-ET-ST6005-1 | HTC-24 / CB-24 | 29209-ST-6005 | 29209-65R-ET-ST6005-01-01 | 13.1 | 29209-ET-ST6005-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | 550 MΩ | 288.1 Ω | 2026-05-18 | [12 empty] | D/32SA2400/21.2M/276/277/1.2M/LS23A/X/N12 | 21.2 m m | Levy Ostrup
EHT Trace | 29209-ET-ST6005-2-1 | 29209-ET-ST6005-2 | HTC-26 / CB-26 | 29209-ST-6005 | 29209-65R-ET-ST6005-02-01 | 13.1 | 29209-ET-ST6005-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | 550 MΩ | 217.5 Ω | 2026-05-18 | [12 empty] | D/32SA2275/23.6M/359/277/1.2M/LS23A/X/N12 | 23.6 m m | Levy Ostrup
Power Cable | 29103-AMB-015 |  | 29103-HTP-102 HTC-01 | 29103-HTP-102 |  | 113 | 29103-AMB-015.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-016 |  | 29103-HTP-102 HTC-03 | 29103-HTP-102 |  | 113 | 29103-AMB-016.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-A001-1-PWK-1 | 29103-ET-A001-1 | 29103-HTP-102 HTC-31 | 29103-HTP-102 |  | 113 | 29103-ET-A001-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-HC1901-1-PWK-1 | 29103-ET-HC1901-1 | 29103-HTP-102 HTC-05 | 29103-HTP-102 |  | 113 | 29103-ET-HC1901-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-HC1902-1-PWK-1 | 29103-ET-HC1902-1 | 29103-AMB-015 | 29103-HTP-102 |  | 113 | 29103-ET-HC1902-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-HC1903-1-PWK-1 | 29103-ET-HC1903-1 | 29103-HTP-102 HTC-04 | 29103-HTP-102 |  | 113 | 29103-ET-HC1903-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-HC1905-1-PWK-1 | 29103-ET-HC1905-1 | 29103-AMB-015 | 29103-HTP-102 |  | 113 | 29103-ET-HC1905-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-HC1906-1-PWK-1 | 29103-ET-HC1906-1 | 29103-HTP-102 HTC-06 | 29103-HTP-102 |  | 113 | 29103-ET-HC1906-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-HC1909-1-PWK-1 | 29103-ET-HC1909-1 | 29103-AMB-015 | 29103-HTP-102 |  | 113 | 29103-ET-HC1909-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-MT0001-1-PWK-1 | 29103-ET-MT0001-1 | 29103-HTP-102 HTC-09 | 29103-HTP-102 |  | 113 | 29103-ET-MT0001-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P001A-1-PWK-1 | 29103-ET-P001A-1 | 29103-HTP-102 HTC-02 | 29103-HTP-102 |  | 113 | 29103-ET-P001A-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P001A-2-PWK-1 | 29103-ET-P001A-2 | 29103-HTP-102 HTC-07 | 29103-HTP-102 |  | 113 | 29103-ET-P001A-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P001A-3-PWK-1 | 29103-ET-P001A-3 | 29103-HTP-102 HTC-08 | 29103-HTP-102 |  | 113 | 29103-ET-P001A-3-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P001A-4-PWK-1 | 29103-ET-P001A-4 | 29103-HTP-102 HTC-13 | 29103-HTP-102 |  | 113 | 29103-ET-P001A-4-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P001B-1-PWK-1 | 29103-ET-P001B-1 | 29103-HTP-102 HTC-10 | 29103-HTP-102 |  | 113 | 29103-ET-P001B-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P001B-2-PWK-1 | 29103-ET-P001B-2 | 29103-HTP-102 HTC-15 | 29103-HTP-102 |  | 113 | 29103-ET-P001B-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P001B-3-PWK-1 | 29103-ET-P001B-3 | 29103-HTP-102 HTC-11 | 29103-HTP-102 |  | 113 | 29103-ET-P001B-3-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P001B-4-PWK-1 | 29103-ET-P001B-4 | 29103-HTP-102 HTC-16 | 29103-HTP-102 |  | 113 | 29103-ET-P001B-4-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1003-1-PWK-1 | 29103-ET-P1003-1 | 29103-HTP-102 HTC-19 | 29103-HTP-102 |  | 113 | 29103-ET-P1003-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-P1004-1-PWK-1 | 29103-ET-P1004-1 | 29103-HTP-102 HTC-20 | 29103-HTP-102 |  | 113 | 29103-ET-P1004-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1920-1-PWK-1 | 29103-ET-P1920-1 | 29103-HTP-102 HTC-22 | 29103-HTP-102 |  | 113 | 29103-ET-P1920-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1920-2-PWK-1 | 29103-ET-P1920-2 | 29103-AMB-016 | 29103-HTP-102 |  | 113 | 29103-ET-P1920-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1901-1-PWK-1 | 29103-ET-PG1901-1 | 29103-AMB-016 | 29103-HTP-102 |  | 113 | 29103-ET-PG1901-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1903-1-PWK-1 | 29103-ET-PG1903-1 | 29103-HTP-102 HTC-12 | 29103-HTP-102 |  | 113 | 29103-ET-PG1903-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST0001-1-PWK-1 | 29103-ET-ST0001-1 | 29103-HTP-102 HTC-14 | 29103-HTP-102 |  | 113 | 29103-ET-ST0001-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST0003-1-PWK-1 | 29103-ET-ST0003-1 | 29103-AMB-016 | 29103-HTP-102 |  | 113 | 29103-ET-ST0003-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1816-1-PWK-1 | 29103-ET-ST1816-1 | 29103-AMB-016 | 29103-HTP-102 |  | 113 | 29103-ET-ST1816-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-V004-1-PWK-1 | 29103-ET-V004-1 | 29103-HTP-102 HTC-30 | 29103-HTP-102 |  | 113 | 29103-ET-V004-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-V004-1-PWK-2 | 29103-ET-V004-1 | 29103-HTP-102 HTC-32 | 29103-HTP-102 |  | 113 | 29103-ET-V004-1-PWK-2.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-V1900-1-PWK-1 | 29103-ET-V1900-1 | 29103-HTP-102 HTC-17 | 29103-HTP-102 |  | 113 | 29103-ET-V1900-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29209-ET-A001-1-PWK-1 | 29209-ET-A001-1 | 29103-HTP-102 HTC-29 | 29103-HTP-102 |  | 113 | 29209-ET-A001-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29209-ET-HC6010-1-PWK-1 | 29209-ET-HC6010-1 | 29103-HTP-102 HTC-25 | 29103-HTP-102 |  | 113 | 29209-ET-HC6010-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29209-ET-P6020-1-PWK-1 | 29209-ET-P6020-1 | 29103-HTP-102 HTC-23 | 29103-HTP-102 |  | 113 | 29209-ET-P6020-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29209-ET-P6021-1-PWK-1 | 29209-ET-P6021-1 | 29103-HTP-102 HTC-18 | 29103-HTP-102 |  | 113 | 29209-ET-P6021-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29209-ET-P6022-1-PWK-1 | 29209-ET-P6022-1 | 29103-HTP-102 HTC-21 | 29103-HTP-102 |  | 113 | 29209-ET-P6022-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29209-ET-PG6003-1-PWK-1 | 29209-ET-PG6003-1 | 29103-HTP-102 HTC-27 | 29103-HTP-102 |  | 113 | 29209-ET-PG6003-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29209-ET-ST6005-1-PWK-1 | 29209-ET-ST6005-1 | 29103-HTP-102 HTC-24 | 29103-HTP-102 |  | 113 | 29209-ET-ST6005-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29209-ET-ST6005-2-PWK-1 | 29209-ET-ST6005-2 | 29103-HTP-102 HTC-26 | 29103-HTP-102 |  | 113 | 29209-ET-ST6005-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
RTD | 29103-ET-HC1901-1-R-1 | 29103-ET-HC1901-1 | 29103-HTP-102 HTC-05 | PRODUCED EMULSION | 29103-65R-ET-HC1901-01-01 | 13.2 | 29103-ET-HC1901-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-MT0001-1-R-1 | 29103-ET-MT0001-1 | 29103-HTP-102 HTC-09 |  | 29103-65R-ET-MT0001-01-01 | 13.2 | 29103-ET-MT0001-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-MT0001-1-R-2 | 29103-ET-MT0001-1 | 29103-HTP-102 I/O-1-3 |  | 29103-65R-ET-MT0001-01-01 | 13.2 | 29103-ET-MT0001-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P001A-2-R-1 | 29103-ET-P001A-2 | 29103-HTP-102 HTC-07 | PRODUCED EMULSION | 29103-65R-ET-P001A-02-01 | 13.2 | 29103-ET-P001A-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P001A-2-R-2 | 29103-ET-P001A-2 | 29103-HTP-102 I/O-1-4 | PRODUCED EMULSION | 29103-65R-ET-P001A-02-01 | 13.2 | 29103-ET-P001A-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P001A-2-R-3 | 29103-ET-P001A-2 | 29103-HTP-102 I/O-2-1 | PRODUCED EMULSION | 29103-65R-ET-P001A-02-01 | 13.2 | 29103-ET-P001A-2-R-3.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P001B-2-R-1 | 29103-ET-P001B-2 | 29103-HTP-102 HTC-15 | PRODUCED EMULSION | 29103-65R-ET-P001B-02-01 | 13.2 | 29103-ET-P001B-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P001B-2-R-2 | 29103-ET-P001B-2 | 29103-HTP-102 I/O-2-4 | PRODUCED EMULSION | 29103-65R-ET-P001B-02-01 | 13.2 | 29103-ET-P001B-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P001B-2-R-3 | 29103-ET-P001B-2 | 29103-HTP-102 I/O-3-1 | PRODUCED EMULSION | 29103-65R-ET-P001B-02-01 | 13.2 | 29103-ET-P001B-2-R-3.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1003-1-R-1 | 29103-ET-P1003-1 | 29103-HTP-102 HTC-19 | PRODUCED EMULSION | 29103-65R-ET-P1003-01-01 | 13.2 | 29103-ET-P1003-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1004-1-R-1 | 29103-ET-P1004-1 | 29103-HTP-102 HTC-20 | PRODUCED EMULSION | 29103-65R-ET-P1004-01-01 | 13.2 | 29103-ET-P1004-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-V004-1-R-1 | 29103-ET-V004-1 | 29103-HTP-102 HTC-30 |  |  | 13.2 | 29103-ET-V004-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-V004-1-R-2 | 29103-ET-V004-1 | 29103-HTP-102 HTC-32 |  |  | 13.2 | 29103-ET-V004-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-V1900-1-R-1 | 29103-ET-V1900-1 | 29103-HTP-102 HTC-17 |  | 29103-65R-ET-V1900-01-01 | 13.2 | 29103-ET-V1900-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29209-ET-P6020-1-R-1 | 29209-ET-P6020-1 | 29103-HTP-102 HTC-23 | PRODUCED EMULSION | 29209-65R-ET-P6020-01-01 | 13.2 | 29209-ET-P6020-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29209-ET-P6020-1-R-2 | 29209-ET-P6020-1 | 29103-HTP-102 HTC-38 | PRODUCED EMULSION | 29209-65R-ET-P6020-01-01 | 13.2 | 29209-ET-P6020-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29209-ET-P6021-1-R-1 | 29209-ET-P6021-1 | 29103-HTP-102 HTC-18 | PRODUCED EMULSION | 29209-65R-ET-P6021-01-01 | 13.2 | 29209-ET-P6021-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29209-ET-P6021-1-R-2 | 29209-ET-P6021-1 | 29103-HTP-102 HTC-39 | PRODUCED EMULSION | 29209-65R-ET-P6021-01-01 | 13.2 | 29209-ET-P6021-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29209-ET-P6022-1-R-1 | 29209-ET-P6022-1 | 29103-HTP-102 HTC-21 | PRODUCED EMULSION | 29209-65R-ET-P6022-01-01 | 13.2 | 29209-ET-P6022-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29209-ET-P6022-1-R-2 | 29209-ET-P6022-1 | 29103-HTP-102 HTC-40 | PRODUCED EMULSION | 29209-65R-ET-P6022-01-01 | 13.2 | 29209-ET-P6022-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29209-ET-PG6003-1-R-1 | 29209-ET-PG6003-1 | 29103-HTP-102 HTC-27 | PRODUCED GAS | 29209-65R-ET-PG6003-01-01 | 13.2 | 29209-ET-PG6003-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29209-ET-PG6003-1-R-2 | 29209-ET-PG6003-1 | 29103-HTP-102 I/O-3-4 | PRODUCED GAS | 29209-65R-ET-PG6003-01-01 | 13.2 | 29209-ET-PG6003-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD Cable | 29103-ET-HC1901-1-R-1 | 29103-ET-HC1901-1 | 29103-HTP-102 HTC-05 | 29103-HTP-102 |  | 113 | 29103-ET-HC1901-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-MT0001-1-R-1 | 29103-ET-MT0001-1 | 29103-HTP-102 HTC-09 | 29103-HTP-102 |  | 113 | 29103-ET-MT0001-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-MT0001-1-R-2 | 29103-ET-MT0001-1 | 29103-HTP-102 I/O-1-3 | 29103-HTP-102 |  | 113 | 29103-ET-MT0001-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P001A-2-R-1 | 29103-ET-P001A-2 | 29103-HTP-102 HTC-07 | 29103-HTP-102 |  | 113 | 29103-ET-P001A-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P001A-2-R-2 | 29103-ET-P001A-2 | 29103-HTP-102 I/O-1-4 | 29103-HTP-102 |  | 113 | 29103-ET-P001A-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P001A-2-R-3 | 29103-ET-P001A-2 | 29103-HTP-102 I/O-2-1 | 29103-HTP-102 |  | 113 | 29103-ET-P001A-2-R-3.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P001B-2-R-1 | 29103-ET-P001B-2 | 29103-HTP-102 HTC-15 | 29103-HTP-102 |  | 113 | 29103-ET-P001B-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P001B-2-R-2 | 29103-ET-P001B-2 | 29103-HTP-102 I/O-2-4 | 29103-HTP-102 |  | 113 | 29103-ET-P001B-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P001B-2-R-3 | 29103-ET-P001B-2 | 29103-HTP-102 I/O-3-1 | 29103-HTP-102 |  | 113 | 29103-ET-P001B-2-R-3.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1003-1-R-1 | 29103-ET-P1003-1 | 29103-HTP-102 HTC-19 | 29103-HTP-102 |  | 113 | 29103-ET-P1003-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1004-1-R-1 | 29103-ET-P1004-1 | 29103-HTP-102 HTC-20 | 29103-HTP-102 |  | 113 | 29103-ET-P1004-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-V004-1-R-1 | 29103-ET-V004-1 | 29103-HTP-102 HTC-30 | 29103-HTP-102 |  | 113 | 29103-ET-V004-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-V004-1-R-2 | 29103-ET-V004-1 | 29103-HTP-102 HTC-32 | 29103-HTP-102 |  | 113 | 29103-ET-V004-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-V1900-1-R-1 | 29103-ET-V1900-1 | 29103-HTP-102 HTC-17 | 29103-HTP-102 |  | 113 | 29103-ET-V1900-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-016 |  | 29103-HTP-102 HTC-02 | 29103-HTP-102 |  | 113 | 29103-RJB-016.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-017 |  | 29103-HTP-102 HTC-10 | 29103-HTP-102 |  | 113 | 29103-RJB-017.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-019 |  | 29103-HTP-102 HTC-08 | 29103-HTP-102 |  | 113 | 29103-RJB-019.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-020 |  | 29103-HTP-102 HTC-13,I/O-2-2, I/O-2-3 | 29103-HTP-102 |  | 113 | 29103-RJB-020.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-021 |  | 29103-HTP-102 HTC-11 | 29103-HTP-102 |  | 113 | 29103-RJB-021.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-022 |  | 29103-HTP-102 HTC-16,I/O-3-2, I/O-3-3 | 29103-HTP-102 |  | 113 | 29103-RJB-022.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29209-ET-P6020-1-R-1 | 29209-ET-P6020-1 | 29103-HTP-102 HTC-23 | 29103-HTP-102 |  | 113 | 29209-ET-P6020-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29209-ET-P6020-1-R-2 | 29209-ET-P6020-1 | 29103-HTP-102 HTC-38 | 29103-HTP-102 |  | 113 | 29209-ET-P6020-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29209-ET-P6021-1-R-1 | 29209-ET-P6021-1 | 29103-HTP-102 HTC-18 | 29103-HTP-102 |  | 113 | 29209-ET-P6021-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29209-ET-P6021-1-R-2 | 29209-ET-P6021-1 | 29103-HTP-102 HTC-39 | 29103-HTP-102 |  | 113 | 29209-ET-P6021-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29209-ET-P6022-1-R-1 | 29209-ET-P6022-1 | 29103-HTP-102 HTC-21 | 29103-HTP-102 |  | 113 | 29209-ET-P6022-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29209-ET-P6022-1-R-2 | 29209-ET-P6022-1 | 29103-HTP-102 HTC-40 | 29103-HTP-102 |  | 113 | 29209-ET-P6022-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29209-ET-PG6003-1-R-1 | 29209-ET-PG6003-1 | 29103-HTP-102 HTC-27 | 29103-HTP-102 |  | 113 | 29209-ET-PG6003-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29209-ET-PG6003-1-R-2 | 29209-ET-PG6003-1 | 29103-HTP-102 I/O-3-4 | 29103-HTP-102 |  | 113 | 29209-ET-PG6003-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup

## 29103-HTP-100
29103-HTP-100
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29103-ET-P1800-4-1 | 29103-ET-P1800-4 | HTC-05 / CB-05 | 29103-P-1800 | 29103-65R-ET-P1800-04-01 | 13.1 | 29103-ET-P1800-4-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/36.8M/2859/277/2.1M/LS23A/X/N12 | 36.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-5-1 | 29103-ET-P1800-5 | HTC-02 / CB-02 | 29103-P-1800 | 29103-65R-ET-P1800-05-01 | 13.1 | 29103-ET-P1800-5-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4583/70.3M/4577/277/2.1M/LS23A/X/N12 | 70.3 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-6-1 | 29103-ET-P1800-6 | HTC-06 / CB-06 | 29103-P-1800 | 29103-65R-ET-P1800-06-01 | 13.1 | 29103-ET-P1800-6-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 15.2 Ω | 2026-05-17 | [12 empty] | D/32SP4583/76.2M/4282/277/2.1M/LS23A/X/N12 | 76.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-7-1 | 29103-ET-P1800-7 | HTC-16 / CB-16 | 29103-P-1810, 29103-P-1800 | 29103-65R-ET-P1800-07-01 | 13.1 | 29103-ET-P1800-7-1.pdf | YES | NO | YES | YES | NO | N/A | N/A | N/A | N/A | YES | NO |  | >2.2 GΩ | 15.1 Ω | 2026-05-17 | 550 MΩ | 15.2 Ω | 2026-09-21 | [9 empty] | D/32SP4583/76.3M/4280/277/2.1M/LS23A/X/N12 | 76.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-3-1 | 29103-ET-PE1802-3 | HTC-03 / CB-03 | 29103-PE-1802 | 29103-65R-ET-PE1802-03-01 | 13.1 | 29103-ET-PE1802-3-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4458/18M/1580/74.1/2.1M/LS23A/X/N12 | 18 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-3-2 | 29103-ET-PE1802-3 | HTC-03 / CB-03 | 29103-PE-1802 | 29103-65R-ET-PE1802-03-01 | 13.1 | 29103-ET-PE1802-3-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4458/49.3M/4329/203/1.2M/LS23A/X/N12 | 49.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-4-1 | 29103-ET-PE1802-4 | HTC-07 / CB-07 | 29103-PE-1802 | 29103-65R-ET-PE1802-04-01 | 13.1 | 29103-ET-PE1802-4-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3150/40.8M/3435/277/1.2M/LS23A/X/N12 | 40.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-5-1 | 29103-ET-PE1802-5 | HTC-17 / CB-17 | 29103-PE-1812, 29103-PE-1802 | 29103-65R-ET-PE1802-05-01 | 13.1 | 29103-ET-PE1802-5-1.pdf | YES | YES | NO | YES | NO | N/A | N/A | N/A | N/A | YES | NO | 1 |  |  |  | 550 MΩ | 14.8 Ω | 2026-09-20 | [9 empty] | D/32SP4458/90.7M/4626/277/1.2M/LS23A/X/N12 | 90.7 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-3-1 | 29103-ET-PE1803-3 | HTC-04 / CB-04 | 29103-PE-1803 | 29103-65R-ET-PE1803-03-01 | 13.1 | 29103-ET-PE1803-3-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3200/6.9M/328/40.2/1.2M/LS23A/X/N12/XNF | 6.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-3-2 | 29103-ET-PE1803-3 | HTC-04 / CB-04 | 29103-PE-2803 | 29103-65R-ET-PE1803-03-01 | 13.1 | 29103-ET-PE1803-3-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/18.4M/874/107/1.2M/LS23A/X/N12/XMN | 18.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-3-3 | 29103-ET-PE1803-3 | HTC-04 / CB-04 | 29103-PE-1803 | 29103-65R-ET-PE1803-03-01 | 13.1 | 29103-ET-PE1803-3-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/14.2M/811/277/1.2M/LS23A/X/N12 | 14.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-3-4 | 29103-ET-PE1803-3 | HTC-04 / CB-04 | 29103-PE-1803 | 29103-65R-ET-PE1803-03-01 | 13.1 | 29103-ET-PE1803-3-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/22.3M/1059/130/1.2M/LS23A/X/N12 | 22.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-5-1 | 29103-ET-PE1803-5 | HTC-08 / CB-08 | 29103-PE-1803 | 29103-65R-ET-PE1803-05-01 | 13.1 | 29103-ET-PE1803-5-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/46.9M/1257/277/1.2M/LS23A/X/N12 | 46.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-6-1 | 29103-ET-PE1803-6 | HTC-09 / CB-09 | 29103-PE-1803 | 29103-65R-ET-PE1803-06-01 | 13.1 | 29103-ET-PE1803-6-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/44.4M/2411/277/1.2M/LS23A/X/N12 | 44.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1806-1-1 | 29103-ET-PE1806-1 | HTC-13 / CB-13 |  | 29103-65R-ET-PE1806-01-01 | 13.1 | 29103-ET-PE1806-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SA2318/12.2M/346/211/1.2M/LS23A/X/N12 | 12.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1806-1-2 | 29103-ET-PE1806-1 | HTC-13 / CB-13 | 29103-PE-1807, 29103-PE-1806 | 29103-65R-ET-PE1806-01-01 | 13.1 | 29103-ET-PE1806-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2318/3.8M/108/65.8/1.2M/LS23A/X/N12 | 3.8 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1801-1-1 | 29103-ET-ST1801-1 | 29103-AMB-013 | 29103-ST-1801, 29103-ST-1800 | 29103-65R-ET-ST1801-01-01 | 13.1 | 29103-ET-ST1801-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2400/22.1M/265/277/1.2M/LS23A/X/N12 | 22.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1803-1-1 | 29103-ET-ST1803-1 | 29103-AMB-013 | 29103-ST-1803 | 29103-65R-ET-ST1803-01-01 | 13.1 | 29103-ET-ST1803-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/22.5M/608/178/1.2M/LS23A/X/N12 | 22.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1803-1-2 | 29103-ET-ST1803-1 | 29103-AMB-013 | 29103-ST-1804 | 29103-65R-ET-ST1803-01-01 | 13.1 | 29103-ET-ST1803-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/12.6M/340/99.4/1.2M/LS23A/X/N12 | 12.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1805-1-1 | 29103-ET-ST1805-1 | 29103-AMB-013 | 29103-ST-1805 | 29103-65R-ET-ST1805-01-01 | 13.1 | 29103-ET-ST1805-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/22.3M/611/177/1.2M/LS23A/X/N12 | 22.3 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1805-1-2 | 29103-ET-ST1805-1 | 29103-AMB-013 | 29103-ST-1806 | 29103-65R-ET-ST1805-01-01 | 13.1 | 29103-ET-ST1805-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/12.6M/345/100/1.2M/LS23A/X/N12 | 12.6 m m | Levy Ostrup
Power Cable | 29103-AMB-013 |  | 29103-HTP-100 HTC-01 | 29103-HTP-100 |  | 113 | 29103-AMB-013.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-P1800-4-PWK-1 | 29103-ET-P1800-4 | 29103-HTP-100 HTC-05 | 29103-HTP-100 |  | 113 | 29103-ET-P1800-4-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1800-5-PWK-1 | 29103-ET-P1800-5 | 29103-HTP-100 HTC-02 | 29103-HTP-100 |  | 113 | 29103-ET-P1800-5-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1800-6-PWK-1 | 29103-ET-P1800-6 | 29103-HTP-100 HTC-06 | 29103-HTP-100 |  | 113 | 29103-ET-P1800-6-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1800-7-PWK-1 | 29103-ET-P1800-7 | 29103-HTP-100 HTC-16 | 29103-HTP-100 |  | 113 | 29103-ET-P1800-7-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1802-3-PWK-1 | 29103-ET-PE1802-3 | 29103-HTP-100 HTC-03 | 29103-HTP-100 |  | 113 | 29103-ET-PE1802-3-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-PE1802-4-PWK-1 | 29103-ET-PE1802-4 | 29103-HTP-100 HTC-07 | 29103-HTP-100 |  | 113 | 29103-ET-PE1802-4-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1802-5-PWK-1 | 29103-ET-PE1802-5 | 29103-HTP-100 HTC-17 | 29103-HTP-100 |  | 113 | 29103-ET-PE1802-5-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1803-3-PWK-1 | 29103-ET-PE1803-3 | 29103-HTP-100 HTC-04 | 29103-HTP-100 |  | 113 | 29103-ET-PE1803-3-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1803-5-PWK-1 | 29103-ET-PE1803-5 | 29103-HTP-100 HTC-08 | 29103-HTP-100 |  | 113 | 29103-ET-PE1803-5-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1803-6-PWK-1 | 29103-ET-PE1803-6 | 29103-HTP-100 HTC-09 | 29103-HTP-100 |  | 113 | 29103-ET-PE1803-6-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1806-1-PWK-1 | 29103-ET-PE1806-1 | 29103-HTP-100 HTC-13 | 29103-HTP-100 |  | 113 | 29103-ET-PE1806-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1801-1-PWK-1 | 29103-ET-ST1801-1 | 29103-AMB-013 | 29103-HTP-100 |  | 113 | 29103-ET-ST1801-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1803-1-PWK-1 | 29103-ET-ST1803-1 | 29103-AMB-013 | 29103-HTP-100 |  | 113 | 29103-ET-ST1803-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1805-1-PWK-1 | 29103-ET-ST1805-1 | 29103-AMB-013 | 29103-HTP-100 |  | 113 | 29103-ET-ST1805-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
RTD | 29103-ET-P1800-4-R-1 | 29103-ET-P1800-4 | 29103-HTP-100 HTC-05 | PRODUCED EMULSION | 29103-65R-ET-P1800-04-01 | 13.2 | 29103-ET-P1800-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1800-5-R-1 | 29103-ET-P1800-5 | 29103-HTP-100 HTC-02 | PRODUCED EMULSION | 29103-65R-ET-P1800-05-01 | 13.2 | 29103-ET-P1800-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1800-6-R-1 | 29103-ET-P1800-6 | 29103-HTP-100 HTC-06 | PRODUCED EMULSION | 29103-65R-ET-P1800-06-01 | 13.2 | 29103-ET-P1800-6-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1800-7-R-1 | 29103-ET-P1800-7 | 29103-HTP-100 HTC-16 | PRODUCED EMULSION | Trace: 29103-ET-P1800-7-1 | 13.2 | 29103-ET-P1800-7-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | [18 empty] | Levy Ostrup | 09/21/2026
RTD | 29103-ET-PE1802-3-R-1 | 29103-ET-PE1802-3 | 29103-HTP-100 HTC-03 | PRODUCED EMULSION | 29103-65R-ET-PE1802-03-01 | 13.2 | 29103-ET-PE1802-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1802-4-R-1 | 29103-ET-PE1802-4 | 29103-HTP-100 HTC-07 | PRODUCED EMULSION | 29103-65R-ET-PE1802-04-01 | 13.2 | 29103-ET-PE1802-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1802-5-R-1 | 29103-ET-PE1802-5 | 29103-HTP-100 HTC-17 / CB-17 | PRODUCED EMULSION | 29103-65R-ET-PE1802-05-01 Rev 1A0 Trace: 29103-ET-PE1802-5-1 | 13.2 | 29103-ET-PE1802-5-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 5 | [17 empty] | Levy Ostrup | 09/20/2026 | P-cable not installed
RTD | 29103-ET-PE1803-3-R-1 | 29103-ET-PE1803-3 | 29103-HTP-100 HTC-04 | PRODUCED EMULSION | 29103-65R-ET-PE1803-03-01 | 13.2 | 29103-ET-PE1803-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1803-3-R-2 | 29103-ET-PE1803-3 | 29103-HTP-100 I/O-1-3 | PRODUCED EMULSION | 29103-65R-ET-PE1803-03-01 | 13.2 | 29103-ET-PE1803-3-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1803-5-R-1 | 29103-ET-PE1803-5 | 29103-HTP-100 HTC-08 | PRODUCED EMULSION | 29103-65R-ET-PE1803-05-01 | 13.2 | 29103-ET-PE1803-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1803-6-R-1 | 29103-ET-PE1803-6 | 29103-HTP-100 HTC-09 | PRODUCED EMULSION | 29103-65R-ET-PE1803-06-01 | 13.2 | 29103-ET-PE1803-6-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1806-1-R-1 | 29103-ET-PE1806-1 | 29103-HTP-100 HTC-10 | PRODUCED EMULSION | 29103-65R-ET-PE1806-01-01 | 13.2 | 29103-ET-PE1806-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD Cable | 29103-ET-P1800-4-R-1 | 29103-ET-P1800-4 | 29103-HTP-100 HTC-05 | 29103-HTP-100 |  | 113 | 29103-ET-P1800-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1800-5-R-1 | 29103-ET-P1800-5 | 29103-HTP-100 HTC-02 | 29103-HTP-100 |  | 113 | 29103-ET-P1800-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1800-6-R-1 | 29103-ET-P1800-6 | 29103-HTP-100 HTC-06 | 29103-HTP-100 |  | 113 | 29103-ET-P1800-6-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1800-7-R-1 | 29103-ET-P1800-7 | 29103-HTP-100 HTC-16 | 29103-HTP-100 |  | 113 | 29103-ET-P1800-7-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1802-3-R-1 | 29103-ET-PE1802-3 | 29103-HTP-100 HTC-03 | 29103-HTP-100 |  | 113 | 29103-ET-PE1802-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1802-4-R-1 | 29103-ET-PE1802-4 | 29103-HTP-100 HTC-07 | 29103-HTP-100 |  | 113 | 29103-ET-PE1802-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1802-5-R-1 | 29103-ET-PE1802-5 | 29103-HTP-100 HTC-17 | 29103-HTP-100 |  | 113 | 29103-ET-PE1802-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1803-3-R-1 | 29103-ET-PE1803-3 | 29103-HTP-100 HTC-04 | 29103-HTP-100 |  | 113 | 29103-ET-PE1803-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1803-3-R-2 | 29103-ET-PE1803-3 | 29103-HTP-100 I/O-1-3 | 29103-HTP-100 |  | 113 | 29103-ET-PE1803-3-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1803-5-R-1 | 29103-ET-PE1803-5 | 29103-HTP-100 HTC-08 | 29103-HTP-100 |  | 113 | 29103-ET-PE1803-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1803-6-R-1 | 29103-ET-PE1803-6 | 29103-HTP-100 HTC-09 | 29103-HTP-100 |  | 113 | 29103-ET-PE1803-6-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1806-1-R-1 | 29103-ET-PE1806-1 | 29103-HTP-100 HTC-10 | 29103-HTP-100 |  | 113 | 29103-ET-PE1806-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup

## 29103-HTP-101
29103-HTP-101
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29103-ET-P1001-1-1 | 29103-ET-P1001-1 | HTC-39 / CB-39 | 29103-P-1001 | 29103-65R-ET-P1001-01-01 | 13.1 | 29103-ET-P1001-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 27.7 Ω | 2026-05-17 | [12 empty] | D/32SQ3150/53.7M/2674/277/2.1M/LS23A/X/N12 | 53.7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1001-1-2 | 29103-ET-P1001-1 | HTC-39 / CB-39 | 29103-P-1001 | 29103-65R-ET-P1001-01-01 | 13.1 | 29103-ET-P1001-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 27.7 Ω | 2026-05-17 | [12 empty] | D/32SQ3150/53.7M/2674/277/2.1M/LS23A/X/N12 | 53.7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1001-2-1 | 29103-ET-P1001-2 | HTC-07 / CB-07 |  | 29103-65R-ET-P1001-02-01 | 13.1 | 29103-ET-P1001-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 121.3 Ω | 2026-05-17 | [12 empty] | D/32SA2275/13.1M/639/277/2.1M/LS23A/X/N12 | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-4-1 | 29103-ET-P2800-4 | HTC-05 / CB-05 | 29103-P-2800 | 29103-65R-ET-P2800-04-01 | 13.1 | 29103-ET-P2800-4-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/36.8M/2859/277/2.1M/LS23A/X/N12 | 36.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-5-1 | 29103-ET-P2800-5 | HTC-02 / CB-02 | 29103-P-2800 | 29103-65R-ET-P2800-05-01 | 13.1 | 29103-ET-P2800-5-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4583/70.3M/4577/277/2.1M/LS23A/X/N12 | 70.3 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-6-1 | 29103-ET-P2800-6 | HTC-06 / CB-06 | 29103-P-2800 | 29103-65R-ET-P2800-06-01 | 13.1 | 29103-ET-P2800-6-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 26.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3150/51.6M/2771/277/2.1M/LS23A/X/N12 | 51.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-6-2 | 29103-ET-P2800-6 | HTC-06 / CB-06 | 29103-P-2800 | 29103-65R-ET-P2800-06-01 | 13.1 | 29103-ET-P2800-6-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 26.8 Ω | 2026-05-17 | [12 empty] | D/32SQ3150/51.6M/2771/277/2.1M/LS23A/X/N12 | 51.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-7-1 | 29103-ET-P2800-7 | HTC-38 / CB-38 | 29103-P-2810, 29103-P-2800 | 29103-65R-ET-P2800-07-01 | 13.1 | 29103-ET-P2800-7-1.pdf | YES | NO | YES | YES | NO | N/A | N/A | N/A | N/A | YES | NO |  | >2.2 GΩ | 23 Ω | 2026-05-17 | 550 MΩ | 23.0 Ω | 2026-09-20 | [9 empty] | D/32SQ3150/45.8M/3092/277/2.1M/LS23A/X/N12 | 45.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-7-2 | 29103-ET-P2800-7 | HTC-38 / CB-38 | 29103-P-2810, 29103-P-2800 | 29103-65R-ET-P2800-07-01 | 13.1 | 29103-ET-P2800-7-2.pdf | YES | NO | YES | YES | NO | N/A | N/A | N/A | N/A | YES | NO |  | >2.2 GΩ | 23.1 Ω | 2026-05-17 | 550 MΩ | 23.1 Ω | 2026-09-20 | [9 empty] | D/32SQ3150/45.8M/3092/277/2.1M/LS23A/X/N12 | 45.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1001-1-1 | 29103-ET-PE1001-1 | HTC-12 / CB-12 | 29103-PE-1002, 29103-PE-1001 | 29103-65R-ET-PE1001-01-01 | 13.1 | 29103-ET-PE1001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3150/51.4M/2781/277/2.1M/LS23A/X/N12 | 51.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1001-1-2 | 29103-ET-PE1001-1 | HTC-12 / CB-12 | 29103-PE-1002, 29103-PE-1001 | 29103-65R-ET-PE1001-01-01 | 13.1 | 29103-ET-PE1001-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3150/51.4M/2781/277/2.1M/LS23A/X/N12 | 51.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1002-1-1 | 29103-ET-PE1002-1 | HTC-23 / CB-23 | 29103-PE-1002 | 29103-65R-ET-PE1002-01-01 | 13.1 | 29103-ET-PE1002-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/13.8M/835/277/2.1M/LS23A/X/N12 | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-4-1 | 29103-ET-PE1803-4 | HTC-18 / CB-18 | 29103-PE-1805 | 29103-65R-ET-PE1803-04-01 | 13.1 | 29103-ET-PE1803-4-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/10.8M/423/87.2/1.2M/LS23A/X/N12/XNF | 10.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-4-2 | 29103-ET-PE1803-4 | HTC-18 / CB-18 | 29103-PE-1805 | 29103-65R-ET-PE1803-04-01 | 13.1 | 29103-ET-PE1803-4-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/15.1M/592/122/1.2M/LS23A/X/N12/XMF | 15.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-4-3 | 29103-ET-PE1803-4 | HTC-18 / CB-18 | 29103-PE-1804, 29103-PE-1803 | 29103-65R-ET-PE1803-04-01 | 13.1 | 29103-ET-PE1803-4-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/8.4M/329/67.8/1.2M/LS23A/X/N12/XMN | 8.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-3-1 | 29103-ET-PE2802-3 | HTC-03 / CB-03 | 29103-PE-2802 | 29103-65R-ET-PE2802-03-01 | 13.1 | 29103-ET-PE2802-3-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4458/18M/1580/74.1/2.1M/LS23A/X/N12 | 18 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-3-2 | 29103-ET-PE2802-3 | HTC-03 / CB-03 | 29103-PE-2802 | 29103-65R-ET-PE2802-03-01 | 13.1 | 29103-ET-PE2802-3-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4458/49.3M/4329/203/1.2M/LS23A/X/N12 | 49.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-4-1 | 29103-ET-PE2802-4 | HTC-10 / CB-10 | 29103-PE-2802 | 29103-65R-ET-PE2802-04-01 | 13.1 | 29103-ET-PE2802-4-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/47.3M/4441/277/1.2M/LS23A/X/N12 | 47.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-5-1 | 29103-ET-PE2802-5 | HTC-37 / CB-37 | 29103-PE-2812, 29103-PE-2802 | 29103-65R-ET-PE2802-05-01 | 13.1 | 29103-ET-PE2802-5-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/51.7M/2094/277/2.1M/LS23A/X/N12 | 51.7 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-5-2 | 29103-ET-PE2802-5 | HTC-37 / CB-37 | 29103-PE-2812, 29103-PE-2802 | 29103-65R-ET-PE2802-05-01 | 13.1 | 29103-ET-PE2802-5-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/51.7M/2094/277/2.1M/LS23A/X/N12 | 51.7 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2803-3-1 | 29103-ET-PE2803-3 | HTC-04 / CB-04 | 29103-PE-2803 | 29103-65R-ET-PE2803-03-01 | 13.1 | 29103-ET-PE2803-3-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3150/53.8M/2668/277/1.2M/LS23A/X/N12 | 53.8 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1809-1-1 | 29103-ET-ST1809-1 | HTC-17 / CB-17 | 29103-ST-1811, 29103-ST-1810, 29103-ST-1809, 29103- SC-1802, 29103-SC-1801 | 29103-65R-ET-ST1809-01-01 | 13.1 | 29103-ET-ST1809-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 95.4 Ω | 2026-05-18 | [12 empty] | D/32SB3700/40.6M/820/277/1.2M/LS23A/X/N12 | 40.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2801-1-1 | 29103-ET-ST2801-1 | 29103-AMB-014 | 29103-ST-2801, 29103-ST-2800 | 29103-65R-ET-ST2801-01-01 | 13.1 | 29103-ET-ST2801-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2400/22.1M/265/277/1.2M/LS23A/X/N12 | 22.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2803-1-1 | 29103-ET-ST2803-1 | 29103-AMB-014 | 29103-ST-2803 | 29103-65R-ET-ST2803-01-01 | 13.1 | 29103-ET-ST2803-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/22.5M/608/178/1.2M/LS23A/X/N12 | 22.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2803-1-2 | 29103-ET-ST2803-1 | 29103-AMB-014 | 29103-ST-2804 | 29103-65R-ET-ST2803-01-01 | 13.1 | 29103-ET-ST2803-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/12.6M/340/99.4/1.2M/LS23A/X/N12 | 12.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2805-1-1 | 29103-ET-ST2805-1 | 29103-AMB-014 | 29103-ST-2805 | 29103-65R-ET-ST2805-01-01 | 13.1 | 29103-ET-ST2805-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/22.3M/611/177/1.2M/LS23A/X/N12 | 22.3 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2805-1-2 | 29103-ET-ST2805-1 | 29103-AMB-014 | 29103-ST-2806 | 29103-65R-ET-ST2805-01-01 | 13.1 | 29103-ET-ST2805-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/12.6M/345/100/1.2M/LS23A/X/N12 | 12.6 m m | Levy Ostrup
EHT Trace | 29103-ET-UT1400-1-1 | 29103-ET-UT1400-1 | HTC-11 / CB-11 |  | 29103-65R-ET-UT1400-01-01 | 13.1 | 29103-ET-UT1400-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20XTVR2-CT | 8.9 m m | Levy Ostrup
Power Cable | 29103-AMB-014 |  | 29103-HTP-101 HTC-01 | 29103-HTP-101 |  | 113 | 29103-AMB-014.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-P1001-1-PWK-1 | 29103-ET-P1001-1 | 29103-HTP-101 HTC-39 | 29103-HTP-101 |  | 113 | 29103-ET-P1001-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-P1001-2-PWK-1 | 29103-ET-P1001-2 | 29103-HTP-101 HTC-07 | 29103-HTP-101 |  | 113 | 29103-ET-P1001-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2800-4-PWK-1 | 29103-ET-P2800-4 | 29103-HTP-101 HTC-05 | 29103-HTP-101 |  | 113 | 29103-ET-P2800-4-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2800-5-PWK-1 | 29103-ET-P2800-5 | 29103-HTP-101 HTC-02 | 29103-HTP-101 |  | 113 | 29103-ET-P2800-5-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2800-6-PWK-1 | 29103-ET-P2800-6 | 29103-HTP-101 HTC-06 | 29103-HTP-101 |  | 113 | 29103-ET-P2800-6-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-P2800-7-PWK-1 | 29103-ET-P2800-7 | 29103-HTP-101 HTC-38 | 29103-HTP-101 |  | 113 | 29103-ET-P2800-7-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-PE1001-1-PWK-1 | 29103-ET-PE1001-1 | 29103-HTP-101 HTC-12 | 29103-HTP-101 |  | 113 | 29103-ET-PE1001-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-PE1002-1-PWK-1 | 29103-ET-PE1002-1 | 29103-HTP-101 HTC-23 | 29103-HTP-101 |  | 113 | 29103-ET-PE1002-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1803-4-PWK-1 | 29103-ET-PE1803-4 | 29103-HTP-101 HTC-18 | 29103-HTP-101 |  | 113 | 29103-ET-PE1803-4-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2802-3-PWK-1 | 29103-ET-PE2802-3 | 29103-HTP-101 HTC-03 | 29103-HTP-101 |  | 113 | 29103-ET-PE2802-3-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-PE2802-4-PWK-1 | 29103-ET-PE2802-4 | 29103-HTP-101 HTC-10 | 29103-HTP-101 |  | 113 | 29103-ET-PE2802-4-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2802-5-PWK-1 | 29103-ET-PE2802-5 | 29103-HTP-101 HTC-37 | 29103-HTP-101 |  | 113 | 29103-ET-PE2802-5-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2803-3-PWK-1 | 29103-ET-PE2803-3 | 29103-HTP-101 HTC-04 | 29103-HTP-101 |  | 113 | 29103-ET-PE2803-3-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1809-1-PWK-1 | 29103-ET-ST1809-1 | 29103-HTP-101 HTC-17 | 29103-HTP-101 |  | 113 | 29103-ET-ST1809-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2801-1-PWK-1 | 29103-ET-ST2801-1 | 29103-AMB-014 | 29103-HTP-101 |  | 113 | 29103-ET-ST2801-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2803-1-PWK-1 | 29103-ET-ST2803-1 | 29103-AMB-014 | 29103-HTP-101 |  | 113 | 29103-ET-ST2803-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2805-1-PWK-1 | 29103-ET-ST2805-1 | 29103-AMB-014 | 29103-HTP-101 |  | 113 | 29103-ET-ST2805-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-UT1400-1-PWK-1 | 29103-ET-UT1400-1 | 29103-HTP-101 HTC-11 | 29103-HTP-101 |  | 113 | 29103-ET-UT1400-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
RTD | 29103-ET-P1001-1-R-1 | 29103-ET-P1001-1 | 29103-HTP-101 HTC-39 | PRODUCED EMULSION | 29103-65R-ET-P1001-01-01 | 13.2 | 29103-ET-P1001-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2800-4-R-1 | 29103-ET-P2800-4 | 29103-HTP-101 HTC-05 | PRODUCED EMULSION | 29103-65R-ET-P2800-04-01 | 13.2 | 29103-ET-P2800-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2800-5-R-1 | 29103-ET-P2800-5 | 29103-HTP-101 HTC-02 | PRODUCED EMULSION | 29103-65R-ET-P2800-05-01 | 13.2 | 29103-ET-P2800-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2800-6-R-1 | 29103-ET-P2800-6 | 29103-HTP-101 HTC-06 | PRODUCED EMULSION | 29103-65R-ET-P2800-06-01 | 13.2 | 29103-ET-P2800-6-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2800-7-R-1 | 29103-ET-P2800-7 | 29103-HTP-101 HTC-38 / CB-38 | PRODUCED EMULSION | 29103-65R-ET-P2800-07-01 Rev 1A0 Trace: 29103-ET-P2800-7-1 | 13.2 | 29103-ET-P2800-7-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | [18 empty] | Levy Ostrup | 09/20/2026
RTD | 29103-ET-P2800-7-R-2 | 29103-ET-P2800-7 | 29103-HTP-101 | PRODUCED EMULSION | Zone drawing: 29103 Trace: 29103-ET-P2800-7-2 | 13.2 | 29103-ET-P2800-7-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | [18 empty] | Levy Ostrup | 09/20/2026
RTD | 29103-ET-PE1001-1-R-1 | 29103-ET-PE1001-1 | 29103-HTP-101 HTC-12 | PRODUCED EMULSION | 29103-65R-ET-PE1001-01-01 | 13.2 | 29103-ET-PE1001-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1001-1-R-2 | 29103-ET-PE1001-1 | 29103-HTP-101 I/O-1-4 | PRODUCED EMULSION | 29103-65R-ET-PE1001-01-01 | 13.2 | 29103-ET-PE1001-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1803-4-R-1 | 29103-ET-PE1803-4 | 29103-HTP-101 HTC-18 | PRODUCED EMULSION | 29103-65R-ET-PE1803-04-01 | 13.2 | 29103-ET-PE1803-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2802-3-R-1 | 29103-ET-PE2802-3 | 29103-HTP-101 HTC-03 | PRODUCED EMULSION | 29103-65R-ET-PE2802-03-01 | 13.2 | 29103-ET-PE2802-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2802-4-R-1 | 29103-ET-PE2802-4 | 29103-HTP-101 HTC-10 | PRODUCED EMULSION | 29103-65R-ET-PE2802-04-01 | 13.2 | 29103-ET-PE2802-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2802-5-R-1 | 29103-ET-PE2802-5 | 29103-HTP-101 HTC-37 | PRODUCED EMULSION | 29103-65R-ET-PE2802-05-01 | 13.2 | 29103-ET-PE2802-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2803-3-R-1 | 29103-ET-PE2803-3 | 29103-HTP-101 HTC-04 | PRODUCED EMULSION | 29103-65R-ET-PE2803-03-01 | 13.2 | 29103-ET-PE2803-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD Cable | 29103-ET-P1001-1-R-1 | 29103-ET-P1001-1 | 29103-HTP-101 HTC-39 | 29103-HTP-101 |  | 113 | 29103-ET-P1001-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2800-4-R-1 | 29103-ET-P2800-4 | 29103-HTP-101 HTC-05 | 29103-HTP-101 |  | 113 | 29103-ET-P2800-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2800-5-R-1 | 29103-ET-P2800-5 | 29103-HTP-101 HTC-02 | 29103-HTP-101 |  | 113 | 29103-ET-P2800-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2800-6-R-1 | 29103-ET-P2800-6 | 29103-HTP-101 HTC-06 | 29103-HTP-101 |  | 113 | 29103-ET-P2800-6-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2800-7-R-1 | 29103-ET-P2800-7 | 29103-HTP-101 HTC-38 | 29103-HTP-101 |  | 113 | 29103-ET-P2800-7-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1001-1-R-1 | 29103-ET-PE1001-1 | 29103-HTP-101 HTC-12 | 29103-HTP-101 |  | 113 | 29103-ET-PE1001-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1001-1-R-2 | 29103-ET-PE1001-1 | 29103-HTP-101 I/O-1-4 | 29103-HTP-101 |  | 113 | 29103-ET-PE1001-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1803-4-R-1 | 29103-ET-PE1803-4 | 29103-HTP-101 HTC-18 | 29103-HTP-101 |  | 113 | 29103-ET-PE1803-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2802-3-R-1 | 29103-ET-PE2802-3 | 29103-HTP-101 HTC-03 | 29103-HTP-101 |  | 113 | 29103-ET-PE2802-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2802-4-R-1 | 29103-ET-PE2802-4 | 29103-HTP-101 HTC-10 | 29103-HTP-101 |  | 113 | 29103-ET-PE2802-4-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2802-5-R-1 | 29103-ET-PE2802-5 | 29103-HTP-101 HTC-37 | 29103-HTP-101 |  | 113 | 29103-ET-PE2802-5-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2803-3-R-1 | 29103-ET-PE2803-3 | 29103-HTP-101 HTC-04 | 29103-HTP-101 |  | 113 | 29103-ET-PE2803-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-015 |  | 29103-HTP-101 HTC-07 | 29103-HTP-101 |  | 113 | 29103-RJB-015.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-024 |  | 29103-HTP-101 I/O-1-3 | 29103-HTP-101 |  | 113 | 29103-RJB-024.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-025 |  | 29103-HTP-101 HTC-23 | 29103-HTP-101 |  | 113 | 29103-RJB-025.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup

## 29103-HTP-004
29103-HTP-004
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29103-ET-FG2101-1-1 | 29103-ET-FG2101-1 | HTC-34 / CB-34 | 29103-FG-2101 | 29103-65R-ET-FG2101-01-01 | 13.1 | 29103-ET-FG2101-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 25.4 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2103-1-1 | 29103-ET-FG2103-1 | HTC-30 / CB-30 | 29103-FG-2103 | 29103-65R-ET-FG2103-01-01 | 13.1 | 29103-ET-FG2103-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 15.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2103-1-2 | 29103-ET-FG2103-1 | HTC-30 / CB-30 | 29103-FG-2103 | 29103-65R-ET-FG2103-01-01 | 13.1 | 29103-ET-FG2103-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 11.7 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2103-1-3 | 29103-ET-FG2103-1 | HTC-30 / CB-30 |  | 29103-65R-ET-FG2103-01-01 | 13.1 | 29103-ET-FG2103-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2103-1-4 | 29103-ET-FG2103-1 | HTC-30 / CB-30 |  | 29103-65R-ET-FG2103-01-01 | 13.1 | 29103-ET-FG2103-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2201-1-1 | 29103-ET-FG2201-1 | 29103-AMB-007 | 29103-FG-2201 | 29103-65R-ET-FG2201-01-01 | 13.1 | 29103-ET-FG2201-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 23.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2201-1-2 | 29103-ET-FG2201-1 | 29103-AMB-007 |  | 29103-65R-ET-FG2201-01-01 | 13.1 | 29103-ET-FG2201-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 1.2 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2203-1-1 | 29103-ET-FG2203-1 | 29103-AMB-007 | 29103-FG-2203 | 29103-65R-ET-FG2203-01-01 | 13.1 | 29103-ET-FG2203-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 11.3 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2203-1-2 | 29103-ET-FG2203-1 | 29103-AMB-007 | 29103-FG-2203 | 29103-65R-ET-FG2203-01-01 | 13.1 | 29103-ET-FG2203-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 12.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2203-1-3 | 29103-ET-FG2203-1 | 29103-AMB-007 |  | 29103-65R-ET-FG2203-01-01 | 13.1 | 29103-ET-FG2203-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2203-1-4 | 29103-ET-FG2203-1 | 29103-AMB-007 |  | 29103-65R-ET-FG2203-01-01 | 13.1 | 29103-ET-FG2203-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2205-1-1 | 29103-ET-FG2205-1 | 29103-AMB-008 | 29103-FG-2206, 29103-FG-2205 | 29103-65R-ET-FG2205-01-01 | 13.1 | 29103-ET-FG2205-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 326.2 Ω | 2026-05-17 | [12 empty] | D/32SA2600/16M/243/277/1.2M/LS23A/X/N12 | 16 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2301-1-1 | 29103-ET-FG2301-1 | 29103-AMB-007 | 29103-FG-2301 | 29103-65R-ET-FG2301-01-01 | 13.1 | 29103-ET-FG2301-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 23.2 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2303-1-1 | 29103-ET-FG2303-1 | 29103-AMB-007 | 29103-FG-2303 | 29103-65R-ET-FG2303-01-01 | 13.1 | 29103-ET-FG2303-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 14 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2303-1-2 | 29103-ET-FG2303-1 | 29103-AMB-007 | 29103-FG-2303 | 29103-65R-ET-FG2303-01-01 | 13.1 | 29103-ET-FG2303-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 17.3 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2303-1-3 | 29103-ET-FG2303-1 | 29103-AMB-007 |  | 29103-65R-ET-FG2303-01-01 | 13.1 | 29103-ET-FG2303-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2303-1-4 | 29103-ET-FG2303-1 | 29103-AMB-007 |  | 29103-65R-ET-FG2303-01-01 | 13.1 | 29103-ET-FG2303-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2405-1-1 | 29103-ET-FG2405-1 | 29103-AMB-010 | 29103-FG-2406, 29103-FG-2405 | 29103-65R-ET-FG2405-01-01 | 13.1 | 29103-ET-FG2405-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 323.8 Ω | 2026-05-17 | [12 empty] | D/32SA2600/16M/243/277/1.2M/LS23A/X/N12 | 16 m m | Levy Ostrup
EHT Trace | 29103-ET-P2101-1-1 | 29103-ET-P2101-1 | HTC-19 / CB-19 | 29103-P-2101 | 29103-65R-ET-P2101-01-01 | 13.1 | 29103-ET-P2101-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.5M/1007/166/1.2M/LS23A/X/N12/XNF | 20.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P2101-1-2 | 29103-ET-P2101-1 | HTC-19 / CB-19 | 29103-P-2101 | 29103-65R-ET-P2101-01-01 | 13.1 | 29103-ET-P2101-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.8M/678/111/1.2M/LS23A/X/N12/XMN | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2104-1-1 | 29103-ET-P2104-1 | HTC-18 / CB-18 | 29103-PE-2101, 29103-P-2104 | 29103-65R-ET-P2104-01-01 | 13.1 | 29103-ET-P2104-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2104-1-2 | 29103-ET-P2104-1 | HTC-18 / CB-18 | 29103-P-2104 | 29103-65R-ET-P2104-01-01 | 13.1 | 29103-ET-P2104-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.9 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/8M/461/78.9/1.2M/LS23A/X/N12/XNF | 8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2104-1-3 | 29103-ET-P2104-1 | HTC-18 / CB-18 | 29103-P-2104 | 29103-65R-ET-P2104-01-01 | 13.1 | 29103-ET-P2104-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/403/69/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2104-1-4 | 29103-ET-P2104-1 | HTC-18 / CB-18 | 29103-P-2104 | 29103-65R-ET-P2104-01-01 | 13.1 | 29103-ET-P2104-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/755/129/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2104-2-1 | 29103-ET-P2104-2 | HTC-25 / CB-25 | 29103-P-2104, 29103-FG-2102 | 29103-65R-ET-P2104-02-01 | 13.1 | 29103-ET-P2104-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 373.5 Ω | 2026-05-17 | [12 empty] | D/32SF1180/6.2M/207/277/1.2M/LS23A/X/N12 | 6.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P2201-1-1 | 29103-ET-P2201-1 | HTC-05 / CB-05 | 29103-P-2201 | 29103-65R-ET-P2201-01-01 | 13.1 | 29103-ET-P2201-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.6M/1001/165/1.2M/LS23A/X/N12/XNF | 20.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P2201-1-2 | 29103-ET-P2201-1 | HTC-05 / CB-05 | 29103-P-2201 | 29103-65R-ET-P2201-01-01 | 13.1 | 29103-ET-P2201-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.9M/676/112/1.2M/LS23A/X/N12/XMN | 13.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2204-1-1 | 29103-ET-P2204-1 | HTC-09 / CB-09 | 29103-PE-2201, 29103-P-2204 | 29103-65R-ET-P2204-01-01 | 13.1 | 29103-ET-P2204-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2204-1-2 | 29103-ET-P2204-1 | HTC-09 / CB-09 | 29103-P-2204 | 29103-65R-ET-P2204-01-01 | 13.1 | 29103-ET-P2204-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 10.5 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/6.5M/416/67.7/1.2M/LS23A/X/N12/XNF | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P2204-1-3 | 29103-ET-P2204-1 | HTC-09 / CB-09 | 29103-P-2204 | 29103-65R-ET-P2204-01-01 | 13.1 | 29103-ET-P2204-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/448/72.9/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2204-1-4 | 29103-ET-P2204-1 | HTC-09 / CB-09 | 29103-P-2204 | 29103-65R-ET-P2204-01-01 | 13.1 | 29103-ET-P2204-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/838/136/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2204-2-1 | 29103-ET-P2204-2 | HTC-26 / CB-26 | 29103-P-2204, 29103-FG-2202 | 29103-65R-ET-P2204-02-01 | 13.1 | 29103-ET-P2204-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 262.8 Ω | 2026-05-17 | [12 empty] | D/32SF1110/7M/299/277/1.2M/LS23A/X/N12 | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2301-1-1 | 29103-ET-P2301-1 | HTC-04 / CB-04 | 29103-P-2301 | 29103-65R-ET-P2301-01-01 | 13.1 | 29103-ET-P2301-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.5M/1007/166/1.2M/LS23A/X/N12/XNF | 20.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P2301-1-2 | 29103-ET-P2301-1 | HTC-04 / CB-04 | 29103-P-2301 | 29103-65R-ET-P2301-01-01 | 13.1 | 29103-ET-P2301-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.8M/678/111/1.2M/LS23A/X/N12/XMN | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2304-1-1 | 29103-ET-P2304-1 | HTC-02 / CB-02 | 29103-PE-2301, 29103-P-2304 | 29103-65R-ET-P2304-01-01 | 13.1 | 29103-ET-P2304-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2304-1-2 | 29103-ET-P2304-1 | HTC-02 / CB-02 | 29103-P-2304 | 29103-65R-ET-P2304-01-01 | 13.1 | 29103-ET-P2304-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.9 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/8M/461/78.9/1.2M/LS23A/X/N12/XNF | 8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2304-1-3 | 29103-ET-P2304-1 | HTC-02 / CB-02 | 29103-P-2304 | 29103-65R-ET-P2304-01-01 | 13.1 | 29103-ET-P2304-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/403/69/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2304-1-4 | 29103-ET-P2304-1 | HTC-02 / CB-02 | 29103-P-2304 | 29103-65R-ET-P2304-01-01 | 13.1 | 29103-ET-P2304-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 21 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/755/129/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2304-2-1 | 29103-ET-P2304-2 | HTC-27 / CB-27 | 29103-P-2304, 29103-FG-2302 | 29103-65R-ET-P2304-02-01 | 13.1 | 29103-ET-P2304-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 374.3 Ω | 2026-05-17 | [12 empty] | D/32SF1180/6.2M/207/277/1.2M/LS23A/X/N12 | 6.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P2404-1-1 | 29103-ET-P2404-1 | HTC-32 / CB-32 | 29103-PE-2401, 29103-P-2404 | 29103-65R-ET-P2404-01-01 | 13.1 | 29103-ET-P2404-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2404-1-2 | 29103-ET-P2404-1 | HTC-32 / CB-32 | 29103-P-2404 | 29103-65R-ET-P2404-01-01 | 13.1 | 29103-ET-P2404-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 10.6 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/6.5M/416/67.7/1.2M/LS23A/X/N12/XNF | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P2404-1-3 | 29103-ET-P2404-1 | HTC-32 / CB-32 | 29103-P-2404 | 29103-65R-ET-P2404-01-01 | 13.1 | 29103-ET-P2404-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.3 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/448/72.9/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2404-1-4 | 29103-ET-P2404-1 | HTC-32 / CB-32 | 29103-P-2404 | 29103-65R-ET-P2404-01-01 | 13.1 | 29103-ET-P2404-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.8 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/838/136/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2404-2-1 | 29103-ET-P2404-2 | HTC-41 / CB-41 | 29103-P-2404, 29103-FG-2402 | 29103-65R-ET-P2404-02-01 | 13.1 | 29103-ET-P2404-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 262.9 Ω | 2026-05-17 | [12 empty] | D/32SF1110/7M/299/277/1.2M/LS23A/X/N12 | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-2-1 | 29103-ET-P2800-2 | HTC-31 / CB-31 | 29103-P-2800 | 29103-65R-ET-P2800-02-01 | 13.1 | 29103-ET-P2800-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/47.1M/2553/207/2.1M/LS23A/X/N12 | 47.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-2-2 | 29103-ET-P2800-2 | HTC-31 / CB-31 | 29103-P-2800 | 29103-65R-ET-P2800-02-01 | 13.1 | 29103-ET-P2800-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/15.9M/862/69.9/2.1M/LS23A/X/N12 | 15.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-3-1 | 29103-ET-P2800-3 | HTC-24 / CB-24 | 29103-P-2800 | 29103-65R-ET-P2800-03-01 | 13.1 | 29103-ET-P2800-3-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/9.7M/555/84.8/2.1M/LS23A/X/N12/XNF | 9.7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-3-2 | 29103-ET-P2800-3 | HTC-24 / CB-24 | 29103-P-2800 | 29103-65R-ET-P2800-03-01 | 13.1 | 29103-ET-P2800-3-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/9.7M/555/84.8/2.1M/LS23A/X/N12/XNF | 9.7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-3-3 | 29103-ET-P2800-3 | HTC-24 / CB-24 | 29103-P-2800 | 29103-65R-ET-P2800-03-01 | 13.1 | 29103-ET-P2800-3-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/22M/1258/192/2.1M/LS23A/X/N12/XMN | 22 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-3-4 | 29103-ET-P2800-3 | HTC-24 / CB-24 | 29103-P-2800 | 29103-65R-ET-P2800-03-01 | 13.1 | 29103-ET-P2800-3-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/22M/1258/192/2.1M/LS23A/X/N12/XMN | 22 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2101-1-1 | 29103-ET-PE2101-1 | HTC-23 / CB-23 | 29103-PE-2101 | 29103-65R-ET-PE2101-01-01 | 13.1 | 29103-ET-PE2101-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.8M/269/277/1.2M/LS23A/X/N12 | 7.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2101-1-2 | 29103-ET-PE2101-1 | HTC-23 / CB-23 | 29103-PE-2101 | 29103-65R-ET-PE2101-01-01 | 13.1 | 29103-ET-PE2101-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/9.5M/505/89.8/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2101-1-3 | 29103-ET-PE2101-1 | HTC-23 / CB-23 | 29103-PE-2101 | 29103-65R-ET-PE2101-01-01 | 13.1 | 29103-ET-PE2101-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/351/62.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2101-1-4 | 29103-ET-PE2101-1 | HTC-23 / CB-23 | 29103-PE-2101 | 29103-65R-ET-PE2101-01-01 | 13.1 | 29103-ET-PE2101-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.2M/702/125/1.2M/LS23A/X/N12/XMN | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2101-2-1 | 29103-ET-PE2101-2 | HTC-16 / CB-16 | 29103-PE-2101 | 29103-65R-ET-PE2101-02-01 | 13.1 | 29103-ET-PE2101-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.5M/2063/277/1.2M/LS23A/X/N12 | 52.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2101-2-2 | 29103-ET-PE2101-2 | HTC-16 / CB-16 | 29103-PE-2101 | 29103-65R-ET-PE2101-02-01 | 13.1 | 29103-ET-PE2101-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.4M/694/277/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2102-1-1 | 29103-ET-PE2102-1 | HTC-20 / CB-20 | 29103-PE-2103, 29103-PE-2102 | 29103-65R-ET-PE2102-01-01 | 13.1 | 29103-ET-PE2102-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/34.9M/1658/277/1.2M/LS23A/X/N12 | 34.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2201-1-1 | 29103-ET-PE2201-1 | HTC-08 / CB-08 | 29103-PE-2201 | 29103-65R-ET-PE2201-01-01 | 13.1 | 29103-ET-PE2201-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.5M/280/277/1.2M/LS23A/X/N12 | 7.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2201-1-2 | 29103-ET-PE2201-1 | HTC-08 / CB-08 | 29103-PE-2201 | 29103-65R-ET-PE2201-01-01 | 13.1 | 29103-ET-PE2201-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/10.8M/522/97.1/1.2M/LS23A/X/N12/XNF | 10.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2201-1-3 | 29103-ET-PE2201-1 | HTC-08 / CB-08 | 29103-PE-2201 | 29103-65R-ET-PE2201-01-01 | 13.1 | 29103-ET-PE2201-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/319/59.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2201-1-4 | 29103-ET-PE2201-1 | HTC-08 / CB-08 | 29103-PE-2201 | 29103-65R-ET-PE2201-01-01 | 13.1 | 29103-ET-PE2201-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.4M/647/121/1.2M/LS23A/X/N12/XMN | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2201-2-1 | 29103-ET-PE2201-2 | HTC-12 / CB-12 | 29103-PE-2201 | 29103-65R-ET-PE2201-02-01 | 13.1 | 29103-ET-PE2201-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.1M/2079/277/1.2M/LS23A/X/N12 | 52.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2201-2-2 | 29103-ET-PE2201-2 | HTC-12 / CB-12 | 29103-PE-2201 | 29103-65R-ET-PE2201-02-01 | 13.1 | 29103-ET-PE2201-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.2M/701/277/1.2M/LS23A/X/N12 | 29.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2202-1-1 | 29103-ET-PE2202-1 | HTC-15 / CB-15 | 29103-PE-2202 | 29103-65R-ET-PE2202-01-01 | 13.1 | 29103-ET-PE2202-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/35.4M/1635/277/1.2M/LS23A/X/N12 | 35.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2301-1-1 | 29103-ET-PE2301-1 | HTC-10 / CB-10 | 29103-PE-2301 | 29103-65R-ET-PE2301-01-01 | 13.1 | 29103-ET-PE2301-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.8M/269/277/1.2M/LS23A/X/N12 | 7.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2301-1-2 | 29103-ET-PE2301-1 | HTC-10 / CB-10 | 29103-PE-2301 | 29103-65R-ET-PE2301-01-01 | 13.1 | 29103-ET-PE2301-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/9.5M/505/89.8/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2301-1-3 | 29103-ET-PE2301-1 | HTC-10 / CB-10 | 29103-PE-2301 | 29103-65R-ET-PE2301-01-01 | 13.1 | 29103-ET-PE2301-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/351/62.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2301-1-4 | 29103-ET-PE2301-1 | HTC-10 / CB-10 | 29103-PE-2301 | 29103-65R-ET-PE2301-01-01 | 13.1 | 29103-ET-PE2301-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.2M/702/125/1.2M/LS23A/X/N12/XMN | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2301-2-1 | 29103-ET-PE2301-2 | HTC-07 / CB-07 | 29103-PE-2301 | 29103-65R-ET-PE2301-02-01 | 13.1 | 29103-ET-PE2301-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.5M/2063/277/1.2M/LS23A/X/N12 | 52.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2301-2-2 | 29103-ET-PE2301-2 | HTC-07 / CB-07 | 29103-PE-2301 | 29103-65R-ET-PE2301-02-01 | 13.1 | 29103-ET-PE2301-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.4M/694/277/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2302-1-1 | 29103-ET-PE2302-1 | HTC-06 / CB-06 | 29103-PE-2303, 29103-PE-2302 | 29103-65R-ET-PE2302-01-01 | 13.1 | 29103-ET-PE2302-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/34.9M/1658/277/1.2M/LS23A/X/N12 | 34.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2401-2-1 | 29103-ET-PE2401-2 | HTC-33 / CB-33 | 29103-PE-2401 | 29103-65R-ET-PE2401-02-01 | 13.1 | 29103-ET-PE2401-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.1M/2079/277/1.2M/LS23A/X/N12 | 52.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2401-2-2 | 29103-ET-PE2401-2 | HTC-33 / CB-33 | 29103-PE-2401 | 29103-65R-ET-PE2401-02-01 | 13.1 | 29103-ET-PE2401-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.2M/701/277/1.2M/LS23A/X/N12 | 29.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2402-1-1 | 29103-ET-PE2402-1 | HTC-35 / CB-35 | 29103-PE-2403, 29103-PE-2402 | 29103-65R-ET-PE2402-01-01 | 13.1 | 29103-ET-PE2402-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/35.4M/1635/277/1.2M/LS23A/X/N12 | 35.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2803-2-1 | 29103-ET-PE2803-2 | HTC-29 / CB-29 | 29103-PE-2803 | 29103-65R-ET-PE2803-02-01 | 13.1 | 29103-ET-PE2803-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/11.3M/542/90.2/1.2M/LS23A/X/N12/XNF | 11.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2803-2-2 | 29103-ET-PE2803-2 | HTC-29 / CB-29 | 29103-PE-2803 | 29103-65R-ET-PE2803-02-01 | 13.1 | 29103-ET-PE2803-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/23.4M/1123/187/1.2M/LS23A/X/N12/XMN | 23.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2101-1-1 | 29103-ET-PG2101-1 | HTC-21 / CB-21 | 29103-PG-2101, 29103-PE-2102, 29103-P-2100 | 29103-65R-ET-PG2101-01-01 | 13.1 | 29103-ET-PG2101-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/90M/3006/277/1.2M/LS23A/X/N12 | 90 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2101-2-1 | 29103-ET-PG2101-2 | HTC-22 / CB-22 | 29103-PG-2101 | 29103-65R-ET-PG2101-02-01 | 13.1 | 29103-ET-PG2101-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 21.7 Ω | 2026-05-18 | [12 empty] | E/32SB3700/9.2M/409/93.3/1.2M/LS23A/X/N12/XNF | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2101-2-2 | 29103-ET-PG2101-2 | HTC-22 / CB-22 | 29103-PG-2101 | 29103-65R-ET-PG2101-02-01 | 13.1 | 29103-ET-PG2101-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 15 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/280/63.9/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2101-2-3 | 29103-ET-PG2101-2 | HTC-22 / CB-22 | 29103-PG-2101 | 29103-65R-ET-PG2101-02-01 | 13.1 | 29103-ET-PG2101-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28.2 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/525/120/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2201-1-1 | 29103-ET-PG2201-1 | HTC-14 / CB-14 | 29103-PG-2201, 29103-PE-2202, 29103-P-2200 | 29103-65R-ET-PG2201-01-01 | 13.1 | 29103-ET-PG2201-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/93.1M/2914/277/1.2M/LS23A/X/N12 | 93.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2201-2-1 | 29103-ET-PG2201-2 | HTC-17 / CB-17 | 29103-PG-2201 | 29103-65R-ET-PG2201-02-01 | 13.1 | 29103-ET-PG2201-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 20.4 Ω | 2026-05-18 | [12 empty] | E/32SB3700/8.6M/401/89.2/1.2M/LS23A/X/N12/XNF | 8.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2201-2-2 | 29103-ET-PG2201-2 | HTC-17 / CB-17 | 29103-PG-2201 | 29103-65R-ET-PG2201-02-01 | 13.1 | 29103-ET-PG2201-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 15 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/294/65.4/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2201-2-3 | 29103-ET-PG2201-2 | HTC-17 / CB-17 | 29103-PG-2201 | 29103-65R-ET-PG2201-02-01 | 13.1 | 29103-ET-PG2201-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28.2 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/550/122/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2301-1-1 | 29103-ET-PG2301-1 | HTC-11 / CB-11 | 29103-PG-2301, 29103-PE-2302, 29103-P-2300 | 29103-65R-ET-PG2301-01-01 | 13.1 | 29103-ET-PG2301-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/90M/3006/277/1.2M/LS23A/X/N12 | 90 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2301-2-1 | 29103-ET-PG2301-2 | HTC-13 / CB-13 | 29103-PG-2301 | 29103-65R-ET-PG2301-02-01 | 13.1 | 29103-ET-PG2301-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 21.7 Ω | 2026-05-18 | [12 empty] | E/32SB3700/9.2M/409/93.3/1.2M/LS23A/X/N12/XNF | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2301-2-2 | 29103-ET-PG2301-2 | HTC-13 / CB-13 | 29103-PG-2301 | 29103-65R-ET-PG2301-02-01 | 13.1 | 29103-ET-PG2301-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 15 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/280/63.9/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2301-2-3 | 29103-ET-PG2301-2 | HTC-13 / CB-13 | 29103-PG-2301 | 29103-65R-ET-PG2301-02-01 | 13.1 | 29103-ET-PG2301-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28.1 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/525/120/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2401-2-1 | 29103-ET-PG2401-2 | HTC-36 / CB-36 | 29103-PG-2401 | 29103-65R-ET-PG2401-02-01 | 13.1 | 29103-ET-PG2401-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 20.5 Ω | 2026-05-18 | [12 empty] | E/32SB3700/8.6M/401/89.2/1.2M/LS23A/X/N12/XNF | 8.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2401-2-2 | 29103-ET-PG2401-2 | HTC-36 / CB-36 | 29103-PG-2401 | 29103-65R-ET-PG2401-02-01 | 13.1 | 29103-ET-PG2401-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 15 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/294/65.4/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2401-2-3 | 29103-ET-PG2401-2 | HTC-36 / CB-36 | 29103-PG-2401 | 29103-65R-ET-PG2401-02-01 | 13.1 | 29103-ET-PG2401-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28.1 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/550/122/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2103-1-1 | 29103-ET-ST2103-1 | 29103-AMB-008 | 29103-ST-2104, 29103-ST-2103 | 29103-65R-ET-ST2103-01-01 | 13.1 | 29103-ET-ST2103-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.5M/282/136/1.2M/LS23A/X/N12/XNF | 17.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2103-1-2 | 29103-ET-ST2103-1 | 29103-AMB-008 | 29103-ST-2104 | 29103-65R-ET-ST2103-01-01 | 13.1 | 29103-ET-ST2103-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/293/141/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2103-1-3 | 29103-ET-ST2103-1 | 29103-AMB-008 | 29103-ST-2103 | 29103-65R-ET-ST2103-01-01 | 13.1 | 29103-ET-ST2103-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 55.4 Ω | 2026-05-18 | [12 empty] | E/32SA2170/9.5M/162/93/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2103-1-4 | 29103-ET-ST2103-1 | 29103-AMB-008 | 29103-ST-2103 | 29103-65R-ET-ST2103-01-01 | 13.1 | 29103-ET-ST2103-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 33.6 Ω | 2026-05-18 | [12 empty] | E/32SA2170/5.7M/97/55.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2103-1-5 | 29103-ET-ST2103-1 | 29103-AMB-008 | 29103-ST-2103 | 29103-65R-ET-ST2103-01-01 | 13.1 | 29103-ET-ST2103-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 76.2 Ω | 2026-05-18 | [12 empty] | D/32SA2170/13.1M/224/128/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2203-1-1 | 29103-ET-ST2203-1 | 29103-AMB-008 | 29103-ST-2204, 29103-ST-2203 | 29103-65R-ET-ST2203-01-01 | 13.1 | 29103-ET-ST2203-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.3M/282/135/1.2M/LS23A/X/N12/XNF | 17.3 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2203-1-2 | 29103-ET-ST2203-1 | 29103-AMB-008 | 29103-ST-2204 | 29103-65R-ET-ST2203-01-01 | 13.1 | 29103-ET-ST2203-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/297/142/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2203-1-3 | 29103-ET-ST2203-1 | 29103-AMB-008 | 29103-ST-2203 | 29103-65R-ET-ST2203-01-01 | 13.1 | 29103-ET-ST2203-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 51.9 Ω | 2026-05-18 | [12 empty] | E/32SA2200/7.6M/127/79.7/1.2M/LS23A/X/N12/XNF | 7.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2203-1-4 | 29103-ET-ST2203-1 | 29103-AMB-008 | 29103-ST-2203 | 29103-65R-ET-ST2203-01-01 | 13.1 | 29103-ET-ST2203-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 38.9 Ω | 2026-05-18 | [12 empty] | E/32SA2200/5.7M/95/59.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2203-1-5 | 29103-ET-ST2203-1 | 29103-AMB-008 | 29103-ST-2203 | 29103-65R-ET-ST2203-01-01 | 13.1 | 29103-ET-ST2203-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 88.2 Ω | 2026-05-18 | [12 empty] | D/32SA2200/13.1M/219/137/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2303-1-1 | 29103-ET-ST2303-1 | 29103-AMB-008 | 29103-ST-2304, 29103-ST-2303 | 29103-65R-ET-ST2303-01-01 | 13.1 | 29103-ET-ST2303-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.5M/282/136/1.2M/LS23A/X/N12/XNF | 17.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2303-1-2 | 29103-ET-ST2303-1 | 29103-AMB-008 | 29103-ST-2304 | 29103-65R-ET-ST2303-01-01 | 13.1 | 29103-ET-ST2303-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/293/141/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2303-1-3 | 29103-ET-ST2303-1 | 29103-AMB-008 | 29103-ST-2303 | 29103-65R-ET-ST2303-01-01 | 13.1 | 29103-ET-ST2303-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 55.1 Ω | 2026-05-18 | [12 empty] | E/32SA2170/9.5M/162/93/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2303-1-4 | 29103-ET-ST2303-1 | 29103-AMB-008 | 29103-ST-2303 | 29103-65R-ET-ST2303-01-01 | 13.1 | 29103-ET-ST2303-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 33.3 Ω | 2026-05-18 | [12 empty] | E/32SA2170/5.7M/97/55.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2303-1-5 | 29103-ET-ST2303-1 | 29103-AMB-008 | 29103-ST-2303 | 29103-65R-ET-ST2303-01-01 | 13.1 | 29103-ET-ST2303-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 76.1 Ω | 2026-05-18 | [12 empty] | D/32SA2170/13.1M/224/128/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2403-1-1 | 29103-ET-ST2403-1 | 29103-AMB-010 | 29103-ST-2404, 29103-ST-2403 | 29103-65R-ET-ST2403-01-01 | 13.1 | 29103-ET-ST2403-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.3M/282/135/1.2M/LS23A/X/N12/XNF | 17.3 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2403-1-2 | 29103-ET-ST2403-1 | 29103-AMB-010 | 29103-ST-2404 | 29103-65R-ET-ST2403-01-01 | 13.1 | 29103-ET-ST2403-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/297/142/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2403-1-3 | 29103-ET-ST2403-1 | 29103-AMB-010 | 29103-ST-2403 | 29103-65R-ET-ST2403-01-01 | 13.1 | 29103-ET-ST2403-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 52.1 Ω | 2026-05-18 | [12 empty] | E/32SA2200/7.6M/127/79.7/1.2M/LS23A/X/N12/XNF | 7.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2403-1-4 | 29103-ET-ST2403-1 | 29103-AMB-010 | 29103-ST-2403 | 29103-65R-ET-ST2403-01-01 | 13.1 | 29103-ET-ST2403-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 38.6 Ω | 2026-05-18 | [12 empty] | E/32SA2200/5.7M/95/59.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2403-1-5 | 29103-ET-ST2403-1 | 29103-AMB-010 | 29103-ST-2403 | 29103-65R-ET-ST2403-01-01 | 13.1 | 29103-ET-ST2403-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 88.2 Ω | 2026-05-18 | [12 empty] | D/32SA2200/13.1M/219/137/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2503-1-1 | 29103-ET-ST2503-1 | 29103-AMB-010 | 29103-ST-2504, 29103-ST-2503 | 29103-65R-ET-ST2503-01-01 | 13.1 | 29103-ET-ST2503-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.5M/282/136/1.2M/LS23A/X/N12/XNF | 17.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2503-1-2 | 29103-ET-ST2503-1 | 29103-AMB-010 | 29103-ST-2504 | 29103-65R-ET-ST2503-01-01 | 13.1 | 29103-ET-ST2503-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/293/141/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2503-1-3 | 29103-ET-ST2503-1 | 29103-AMB-010 | 29103-ST-2503 | 29103-65R-ET-ST2503-01-01 | 13.1 | 29103-ET-ST2503-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 55.3 Ω | 2026-05-18 | [12 empty] | E/32SA2170/9.5M/162/93/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2503-1-4 | 29103-ET-ST2503-1 | 29103-AMB-010 | 29103-ST-2503 | 29103-65R-ET-ST2503-01-01 | 13.1 | 29103-ET-ST2503-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 33.2 Ω | 2026-05-18 | [12 empty] | E/32SA2170/5.7M/97/55.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2503-1-5 | 29103-ET-ST2503-1 | 29103-AMB-010 | 29103-ST-2503 | 29103-65R-ET-ST2503-01-01 | 13.1 | 29103-ET-ST2503-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 76.1 Ω | 2026-05-18 | [12 empty] | D/32SA2170/13.1M/224/128/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
Power Cable | 29103-AMB-007 |  | 29103-HTP-004 HTC-01 | 29103-HTP-004 |  | 113 | 29103-AMB-007.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-008 |  | 29103-HTP-004 HTC-03 | 29103-HTP-004 |  | 113 | 29103-AMB-008.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-010 |  | 29103-HTP-004 HTC-28 | 29103-HTP-004 |  | 113 | 29103-AMB-010.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-FG2101-1-PWK-1 | 29103-ET-FG2101-1 | 29103-HTP-004 HTC-34 | 29103-HTP-004 |  | 113 | 29103-ET-FG2101-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2103-1-PWK-1 | 29103-ET-FG2103-1 | 29103-HTP-004 HTC-30 | 29103-HTP-004 |  | 113 | 29103-ET-FG2103-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2201-1-PWK-1 | 29103-ET-FG2201-1 | 29103-AMB-007 | 29103-HTP-004 |  | 113 | 29103-ET-FG2201-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2203-1-PWK-1 | 29103-ET-FG2203-1 | 29103-AMB-007 | 29103-HTP-004 |  | 113 | 29103-ET-FG2203-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2205-1-PWK-1 | 29103-ET-FG2205-1 | 29103-AMB-008 | 29103-HTP-004 |  | 113 | 29103-ET-FG2205-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2301-1-PWK-1 | 29103-ET-FG2301-1 | 29103-AMB-007 | 29103-HTP-004 |  | 113 | 29103-ET-FG2301-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2303-1-PWK-1 | 29103-ET-FG2303-1 | 29103-AMB-007 | 29103-HTP-004 |  | 113 | 29103-ET-FG2303-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2405-1-PWK-1 | 29103-ET-FG2405-1 | 29103-AMB-010 | 29103-HTP-004 |  | 113 | 29103-ET-FG2405-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2101-1-PWK-1 | 29103-ET-P2101-1 | 29103-HTP-004 HTC-19 | 29103-HTP-004 |  | 113 | 29103-ET-P2101-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2104-1-PWK-1 | 29103-ET-P2104-1 | 29103-HTP-004 HTC-18 | 29103-HTP-004 |  | 113 | 29103-ET-P2104-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2104-2-PWK-1 | 29103-ET-P2104-2 | 29103-HTP-004 HTC-25 | 29103-HTP-004 |  | 113 | 29103-ET-P2104-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2201-1-PWK-1 | 29103-ET-P2201-1 | 29103-HTP-004 HTC-05 | 29103-HTP-004 |  | 113 | 29103-ET-P2201-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2204-1-PWK-1 | 29103-ET-P2204-1 | 29103-HTP-004 HTC-09 | 29103-HTP-004 |  | 113 | 29103-ET-P2204-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2204-2-PWK-1 | 29103-ET-P2204-2 | 29103-HTP-004 HTC-26 | 29103-HTP-004 |  | 113 | 29103-ET-P2204-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2301-1-PWK-1 | 29103-ET-P2301-1 | 29103-HTP-004 HTC-04 | 29103-HTP-004 |  | 113 | 29103-ET-P2301-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2304-1-PWK-1 | 29103-ET-P2304-1 | 29103-HTP-004 HTC-02 | 29103-HTP-004 |  | 113 | 29103-ET-P2304-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2304-2-PWK-1 | 29103-ET-P2304-2 | 29103-HTP-004 HTC-27 | 29103-HTP-004 |  | 113 | 29103-ET-P2304-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2404-1-PWK-1 | 29103-ET-P2404-1 | 29103-HTP-004 HTC-32 | 29103-HTP-004 |  | 113 | 29103-ET-P2404-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2404-2-PWK-1 | 29103-ET-P2404-2 | 29103-HTP-004 HTC-41 | 29103-HTP-004 |  | 113 | 29103-ET-P2404-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2800-2-PWK-1 | 29103-ET-P2800-2 | 29103-HTP-004 HTC-31 | 29103-HTP-004 |  | 113 | 29103-ET-P2800-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2800-3-PWK-1 | 29103-ET-P2800-3 | 29103-HTP-004 HTC-24 | 29103-HTP-004 |  | 113 | 29103-ET-P2800-3-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2101-1-PWK-1 | 29103-ET-PE2101-1 | 29103-HTP-004 HTC-23 | 29103-HTP-004 |  | 113 | 29103-ET-PE2101-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2101-2-PWK-1 | 29103-ET-PE2101-2 | 29103-HTP-004 HTC-16 | 29103-HTP-004 |  | 113 | 29103-ET-PE2101-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2102-1-PWK-1 | 29103-ET-PE2102-1 | 29103-HTP-004 HTC-20 | 29103-HTP-004 |  | 113 | 29103-ET-PE2102-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2201-1-PWK-1 | 29103-ET-PE2201-1 | 29103-HTP-004 HTC-08 | 29103-HTP-004 |  | 113 | 29103-ET-PE2201-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2201-2-PWK-1 | 29103-ET-PE2201-2 | 29103-HTP-004 HTC-12 | 29103-HTP-004 |  | 113 | 29103-ET-PE2201-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2202-1-PWK-1 | 29103-ET-PE2202-1 | 29103-HTP-004 HTC-15 | 29103-HTP-004 |  | 113 | 29103-ET-PE2202-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2301-1-PWK-1 | 29103-ET-PE2301-1 | 29103-HTP-004 HTC-10 | 29103-HTP-004 |  | 113 | 29103-ET-PE2301-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2301-2-PWK-1 | 29103-ET-PE2301-2 | 29103-HTP-004 HTC-07 | 29103-HTP-004 |  | 113 | 29103-ET-PE2301-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2302-1-PWK-1 | 29103-ET-PE2302-1 | 29103-HTP-004 HTC-06 | 29103-HTP-004 |  | 113 | 29103-ET-PE2302-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2401-2-PWK-1 | 29103-ET-PE2401-2 | 29103-HTP-004 HTC-33 | 29103-HTP-004 |  | 113 | 29103-ET-PE2401-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2402-1-PWK-1 | 29103-ET-PE2402-1 | 29103-HTP-004 HTC-35 | 29103-HTP-004 |  | 113 | 29103-ET-PE2402-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2803-2-PWK-1 | 29103-ET-PE2803-2 | 29103-HTP-004 HTC-29 | 29103-HTP-004 |  | 113 | 29103-ET-PE2803-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2101-1-PWK-1 | 29103-ET-PG2101-1 | 29103-HTP-004 HTC-21 | 29103-HTP-004 |  | 113 | 29103-ET-PG2101-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2101-2-PWK-1 | 29103-ET-PG2101-2 | 29103-HTP-004 HTC-22 | 29103-HTP-004 |  | 113 | 29103-ET-PG2101-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2201-1-PWK-1 | 29103-ET-PG2201-1 | 29103-HTP-004 HTC-14 | 29103-HTP-004 |  | 113 | 29103-ET-PG2201-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2201-2-PWK-1 | 29103-ET-PG2201-2 | 29103-HTP-004 HTC-17 | 29103-HTP-004 |  | 113 | 29103-ET-PG2201-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2301-1-PWK-1 | 29103-ET-PG2301-1 | 29103-HTP-004 HTC-11 | 29103-HTP-004 |  | 113 | 29103-ET-PG2301-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2301-2-PWK-1 | 29103-ET-PG2301-2 | 29103-HTP-004 HTC-13 | 29103-HTP-004 |  | 113 | 29103-ET-PG2301-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2401-2-PWK-1 | 29103-ET-PG2401-2 | 29103-HTP-004 HTC-36 | 29103-HTP-004 |  | 113 | 29103-ET-PG2401-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2103-1-PWK-1 | 29103-ET-ST2103-1 | 29103-AMB-008 | 29103-HTP-004 |  | 113 | 29103-ET-ST2103-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2203-1-PWK-1 | 29103-ET-ST2203-1 | 29103-AMB-008 | 29103-HTP-004 |  | 113 | 29103-ET-ST2203-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2303-1-PWK-1 | 29103-ET-ST2303-1 | 29103-AMB-008 | 29103-HTP-004 |  | 113 | 29103-ET-ST2303-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2403-1-PWK-1 | 29103-ET-ST2403-1 | 29103-AMB-010 | 29103-HTP-004 |  | 113 | 29103-ET-ST2403-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2503-1-PWK-1 | 29103-ET-ST2503-1 | 29103-AMB-010 | 29103-HTP-004 |  | 113 | 29103-ET-ST2503-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
RTD | 29103-ET-P2101-1-R-1 | 29103-ET-P2101-1 | 29103-HTP-004 HTC-19 | PRODUCED EMULSION | 29103-65R-ET-P2101-01-01 | 13.2 | 29103-ET-P2101-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2104-1-R-1 | 29103-ET-P2104-1 | 29103-HTP-004 HTC-18 | PRODUCED EMULSION | 29103-65R-ET-P2104-01-01 | 13.2 | 29103-ET-P2104-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2104-1-R-2 | 29103-ET-P2104-1 | 29103-HTP-004 I/O-2-1 | PRODUCED EMULSION | 29103-65R-ET-P2104-01-01 | 13.2 | 29103-ET-P2104-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2104-2-R-1 | 29103-ET-P2104-2 | 29103-HTP-004 HTC-25 | PRODUCED EMULSION | 29103-65R-ET-P2104-02-01 | 13.2 | 29103-ET-P2104-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2104-2-R-2 | 29103-ET-P2104-2 | 29103-HTP-004 I/O-4-3 | PRODUCED EMULSION | 29103-65R-ET-P2104-02-01 | 13.2 | 29103-ET-P2104-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2201-1-R-1 | 29103-ET-P2201-1 | 29103-HTP-004 HTC-05 | PRODUCED EMULSION | 29103-65R-ET-P2201-01-01 | 13.2 | 29103-ET-P2201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2204-1-R-1 | 29103-ET-P2204-1 | 29103-HTP-004 HTC-09 | PRODUCED EMULSION | 29103-65R-ET-P2204-01-01 | 13.2 | 29103-ET-P2204-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2204-1-R-2 | 29103-ET-P2204-1 | 29103-HTP-004 I/O-1-4 | PRODUCED EMULSION | 29103-65R-ET-P2204-01-01 | 13.2 | 29103-ET-P2204-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2204-2-R-1 | 29103-ET-P2204-2 | 29103-HTP-004 HTC-26 | PRODUCED EMULSION | 29103-65R-ET-P2204-02-01 | 13.2 | 29103-ET-P2204-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2204-2-R-2 | 29103-ET-P2204-2 | 29103-HTP-004 I/O-4-4 | PRODUCED EMULSION | 29103-65R-ET-P2204-02-01 | 13.2 | 29103-ET-P2204-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2301-1-R-1 | 29103-ET-P2301-1 | 29103-HTP-004 HTC-04 | PRODUCED EMULSION | 29103-65R-ET-P2301-01-01 | 13.2 | 29103-ET-P2301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2304-1-R-1 | 29103-ET-P2304-1 | 29103-HTP-004 HTC-02 | PRODUCED EMULSION | 29103-65R-ET-P2304-01-01 | 13.2 | 29103-ET-P2304-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2304-1-R-2 | 29103-ET-P2304-1 | 29103-HTP-004 I/O-1-3 | PRODUCED EMULSION | 29103-65R-ET-P2304-01-01 | 13.2 | 29103-ET-P2304-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2304-2-R-1 | 29103-ET-P2304-2 | 29103-HTP-004 HTC-27 | PRODUCED EMULSION | 29103-65R-ET-P2304-02-01 | 13.2 | 29103-ET-P2304-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2304-2-R-2 | 29103-ET-P2304-2 | 29103-HTP-004 HTC-28 | PRODUCED EMULSION | 29103-65R-ET-P2304-02-01 | 13.2 | 29103-ET-P2304-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2404-1-R-1 | 29103-ET-P2404-1 | 29103-HTP-004 HTC-32 | PRODUCED EMULSION | 29103-65R-ET-P2404-01-01 | 13.2 | 29103-ET-P2404-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2404-1-R-2 | 29103-ET-P2404-1 | 29103-HTP-004 HTC-01 | PRODUCED EMULSION | 29103-65R-ET-P2404-01-01 | 13.2 | 29103-ET-P2404-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2404-2-R-1 | 29103-ET-P2404-2 | 29103-HTP-004 HTC-41 | PRODUCED EMULSION | 29103-65R-ET-P2404-02-01 | 13.2 | 29103-ET-P2404-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2404-2-R-2 | 29103-ET-P2404-2 | 29103-HTP-004 HTC-03 | PRODUCED EMULSION | 29103-65R-ET-P2404-02-01 | 13.2 | 29103-ET-P2404-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2800-2-R-1 | 29103-ET-P2800-2 | 29103-HTP-004 HTC-31 | PRODUCED EMULSION | 29103-65R-ET-P2800-02-01 | 13.2 | 29103-ET-P2800-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2800-3-R-1 | 29103-ET-P2800-3 | 29103-HTP-004 HTC-24 | PRODUCED EMULSION | 29103-65R-ET-P2800-03-01 | 13.2 | 29103-ET-P2800-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2101-1-R-1 | 29103-ET-PE2101-1 | 29103-HTP-004 HTC-23 | PRODUCED EMULSION | 29103-65R-ET-PE2101-01-01 | 13.2 | 29103-ET-PE2101-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2101-2-R-2 | 29103-ET-PE2101-2 | 29103-HTP-004 I/O-3-2 | PRODUCED EMULSION | 29103-65R-ET-PE2101-02-01 | 13.2 | 29103-ET-PE2101-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2102-1-R-1 | 29103-ET-PE2102-1 | 29103-HTP-004 HTC-20 | PRODUCED EMULSION | 29103-65R-ET-PE2102-01-01 | 13.2 | 29103-ET-PE2102-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2102-1-R-2 | 29103-ET-PE2102-1 | 29103-HTP-004 I/O-3-3 | PRODUCED EMULSION | 29103-65R-ET-PE2102-01-01 | 13.2 | 29103-ET-PE2102-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2201-1-R-1 | 29103-ET-PE2201-1 | 29103-HTP-004 HTC-08 | PRODUCED EMULSION | 29103-65R-ET-PE2201-01-01 | 13.2 | 29103-ET-PE2201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2201-2-R-2 | 29103-ET-PE2201-2 | 29103-HTP-004 I/O-2-4 | PRODUCED EMULSION | 29103-65R-ET-PE2201-02-01 | 13.2 | 29103-ET-PE2201-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2202-1-R-1 | 29103-ET-PE2202-1 | 29103-HTP-004 HTC-15 | PRODUCED EMULSION | 29103-65R-ET-PE2202-01-01 | 13.2 | 29103-ET-PE2202-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2202-1-R-2 | 29103-ET-PE2202-1 | 29103-HTP-004 I/O-3-1 | PRODUCED EMULSION | 29103-65R-ET-PE2202-01-01 | 13.2 | 29103-ET-PE2202-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2301-1-R-1 | 29103-ET-PE2301-1 | 29103-HTP-004 HTC-10 | PRODUCED EMULSION | 29103-65R-ET-PE2301-01-01 | 13.2 | 29103-ET-PE2301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2301-2-R-2 | 29103-ET-PE2301-2 | 29103-HTP-004 I/O-2-2 | PRODUCED EMULSION | 29103-65R-ET-PE2301-02-01 | 13.2 | 29103-ET-PE2301-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2302-1-R-1 | 29103-ET-PE2302-1 | 29103-HTP-004 HTC-06 | PRODUCED EMULSION | 29103-65R-ET-PE2302-01-01 | 13.2 | 29103-ET-PE2302-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2302-1-R-2 | 29103-ET-PE2302-1 | 29103-HTP-004 I/O-2-3 | PRODUCED EMULSION | 29103-65R-ET-PE2302-01-01 | 13.2 | 29103-ET-PE2302-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2401-2-R-2 | 29103-ET-PE2401-2 | 29103-HTP-004 HTC-59 | PRODUCED EMULSION | 29103-65R-ET-PE2401-02-01 | 13.2 | 29103-ET-PE2401-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2402-1-R-1 | 29103-ET-PE2402-1 | 29103-HTP-004 HTC-35 | PRODUCED EMULSION | 29103-65R-ET-PE2402-01-01 | 13.2 | 29103-ET-PE2402-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2402-1-R-2 | 29103-ET-PE2402-1 | 29103-HTP-004 HTC-60 | PRODUCED EMULSION | 29103-65R-ET-PE2402-01-01 | 13.2 | 29103-ET-PE2402-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2803-2-R-1 | 29103-ET-PE2803-2 | 29103-HTP-004 HTC-29 | PRODUCED EMULSION | 29103-65R-ET-PE2803-02-01 | 13.2 | 29103-ET-PE2803-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2101-1-R-1 | 29103-ET-PG2101-1 | 29103-HTP-004 HTC-21 | PRODUCED GAS | 29103-65R-ET-PG2101-01-01 | 13.2 | 29103-ET-PG2101-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2101-1-R-2 | 29103-ET-PG2101-1 | 29103-HTP-004 I/O-4-2 | PRODUCED GAS | 29103-65R-ET-PG2101-01-01 | 13.2 | 29103-ET-PG2101-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2101-2-R-1 | 29103-ET-PG2101-2 | 29103-HTP-004 HTC-22 | PRODUCED GAS | 29103-65R-ET-PG2101-02-01 | 13.2 | 29103-ET-PG2101-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2201-1-R-1 | 29103-ET-PG2201-1 | 29103-HTP-004 HTC-14 | PRODUCED GAS | 29103-65R-ET-PG2201-01-01 | 13.2 | 29103-ET-PG2201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2201-1-R-2 | 29103-ET-PG2201-1 | 29103-HTP-004 I/O-4-1 | PRODUCED GAS | 29103-65R-ET-PG2201-01-01 | 13.2 | 29103-ET-PG2201-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2201-2-R-1 | 29103-ET-PG2201-2 | 29103-HTP-004 HTC-17 | PRODUCED GAS | 29103-65R-ET-PG2201-02-01 | 13.2 | 29103-ET-PG2201-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2301-1-R-1 | 29103-ET-PG2301-1 | 29103-HTP-004 HTC-11 | PRODUCED GAS | 29103-65R-ET-PG2301-01-01 | 13.2 | 29103-ET-PG2301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2301-1-R-2 | 29103-ET-PG2301-1 | 29103-HTP-004 I/O-3-4 | PRODUCED GAS | 29103-65R-ET-PG2301-01-01 | 13.2 | 29103-ET-PG2301-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2301-2-R-1 | 29103-ET-PG2301-2 | 29103-HTP-004 HTC-13 | PRODUCED GAS | 29103-65R-ET-PG2301-02-01 | 13.2 | 29103-ET-PG2301-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2401-2-R-1 | 29103-ET-PG2401-2 | 29103-HTP-004 HTC-36 | PRODUCED GAS | 29103-65R-ET-PG2401-02-01 | 13.2 | 29103-ET-PG2401-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD Cable | 29103-ET-P2101-1-R-1 | 29103-ET-P2101-1 | 29103-HTP-004 HTC-19 | 29103-HTP-004 |  | 113 | 29103-ET-P2101-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2104-1-R-1 | 29103-ET-P2104-1 | 29103-HTP-004 HTC-18 | 29103-HTP-004 |  | 113 | 29103-ET-P2104-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2104-1-R-2 | 29103-ET-P2104-1 | 29103-HTP-004 I/O-2-1 | 29103-HTP-004 |  | 113 | 29103-ET-P2104-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2104-2-R-1 | 29103-ET-P2104-2 | 29103-HTP-004 HTC-25 | 29103-HTP-004 |  | 113 | 29103-ET-P2104-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2104-2-R-2 | 29103-ET-P2104-2 | 29103-HTP-004 I/O-4-3 | 29103-HTP-004 |  | 113 | 29103-ET-P2104-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2201-1-R-1 | 29103-ET-P2201-1 | 29103-HTP-004 HTC-05 | 29103-HTP-004 |  | 113 | 29103-ET-P2201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2204-1-R-1 | 29103-ET-P2204-1 | 29103-HTP-004 HTC-09 | 29103-HTP-004 |  | 113 | 29103-ET-P2204-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2204-1-R-2 | 29103-ET-P2204-1 | 29103-HTP-004 I/O-1-4 | 29103-HTP-004 |  | 113 | 29103-ET-P2204-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2204-2-R-1 | 29103-ET-P2204-2 | 29103-HTP-004 HTC-26 | 29103-HTP-004 |  | 113 | 29103-ET-P2204-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2204-2-R-2 | 29103-ET-P2204-2 | 29103-HTP-004 I/O-4-4 | 29103-HTP-004 |  | 113 | 29103-ET-P2204-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2301-1-R-1 | 29103-ET-P2301-1 | 29103-HTP-004 HTC-04 | 29103-HTP-004 |  | 113 | 29103-ET-P2301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2304-1-R-1 | 29103-ET-P2304-1 | 29103-HTP-004 HTC-02 | 29103-HTP-004 |  | 113 | 29103-ET-P2304-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2304-1-R-2 | 29103-ET-P2304-1 | 29103-HTP-004 I/O-1-3 | 29103-HTP-004 |  | 113 | 29103-ET-P2304-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2304-2-R-1 | 29103-ET-P2304-2 | 29103-HTP-004 HTC-27 | 29103-HTP-004 |  | 113 | 29103-ET-P2304-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2304-2-R-2 | 29103-ET-P2304-2 | 29103-HTP-004 HTC-28 | 29103-HTP-004 |  | 113 | 29103-ET-P2304-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2404-1-R-1 | 29103-ET-P2404-1 | 29103-HTP-004 HTC-32 | 29103-HTP-004 |  | 113 | 29103-ET-P2404-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2404-1-R-2 | 29103-ET-P2404-1 | 29103-HTP-004 HTC-01 | 29103-HTP-004 |  | 113 | 29103-ET-P2404-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2404-2-R-1 | 29103-ET-P2404-2 | 29103-HTP-004 HTC-41 | 29103-HTP-004 |  | 113 | 29103-ET-P2404-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2404-2-R-2 | 29103-ET-P2404-2 | 29103-HTP-004 HTC-03 | 29103-HTP-004 |  | 113 | 29103-ET-P2404-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2800-2-R-1 | 29103-ET-P2800-2 | 29103-HTP-004 HTC-31 | 29103-HTP-004 |  | 113 | 29103-ET-P2800-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2800-3-R-1 | 29103-ET-P2800-3 | 29103-HTP-004 HTC-24 | 29103-HTP-004 |  | 113 | 29103-ET-P2800-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2101-1-R-1 | 29103-ET-PE2101-1 | 29103-HTP-004 HTC-23 | 29103-HTP-004 |  | 113 | 29103-ET-PE2101-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2101-2-R-2 | 29103-ET-PE2101-2 | 29103-HTP-004 I/O-3-2 | 29103-HTP-004 |  | 113 | 29103-ET-PE2101-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2102-1-R-1 | 29103-ET-PE2102-1 | 29103-HTP-004 HTC-20 | 29103-HTP-004 |  | 113 | 29103-ET-PE2102-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2102-1-R-2 | 29103-ET-PE2102-1 | 29103-HTP-004 I/O-3-3 | 29103-HTP-004 |  | 113 | 29103-ET-PE2102-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2201-1-R-1 | 29103-ET-PE2201-1 | 29103-HTP-004 HTC-08 | 29103-HTP-004 |  | 113 | 29103-ET-PE2201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2201-2-R-2 | 29103-ET-PE2201-2 | 29103-HTP-004 I/O-2-4 | 29103-HTP-004 |  | 113 | 29103-ET-PE2201-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2202-1-R-1 | 29103-ET-PE2202-1 | 29103-HTP-004 HTC-15 | 29103-HTP-004 |  | 113 | 29103-ET-PE2202-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2202-1-R-2 | 29103-ET-PE2202-1 | 29103-HTP-004 I/O-3-1 | 29103-HTP-004 |  | 113 | 29103-ET-PE2202-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2301-1-R-1 | 29103-ET-PE2301-1 | 29103-HTP-004 HTC-10 | 29103-HTP-004 |  | 113 | 29103-ET-PE2301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2301-2-R-2 | 29103-ET-PE2301-2 | 29103-HTP-004 I/O-2-2 | 29103-HTP-004 |  | 113 | 29103-ET-PE2301-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2302-1-R-1 | 29103-ET-PE2302-1 | 29103-HTP-004 HTC-06 | 29103-HTP-004 |  | 113 | 29103-ET-PE2302-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2302-1-R-2 | 29103-ET-PE2302-1 | 29103-HTP-004 I/O-2-3 | 29103-HTP-004 |  | 113 | 29103-ET-PE2302-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2401-2-R-2 | 29103-ET-PE2401-2 | 29103-HTP-004 HTC-59 | 29103-HTP-004 |  | 113 | 29103-ET-PE2401-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2402-1-R-1 | 29103-ET-PE2402-1 | 29103-HTP-004 HTC-35 | 29103-HTP-004 |  | 113 | 29103-ET-PE2402-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2402-1-R-2 | 29103-ET-PE2402-1 | 29103-HTP-004 HTC-60 | 29103-HTP-004 |  | 113 | 29103-ET-PE2402-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2803-2-R-1 | 29103-ET-PE2803-2 | 29103-HTP-004 HTC-29 | 29103-HTP-004 |  | 113 | 29103-ET-PE2803-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2101-1-R-1 | 29103-ET-PG2101-1 | 29103-HTP-004 HTC-21 | 29103-HTP-004 |  | 113 | 29103-ET-PG2101-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2101-1-R-2 | 29103-ET-PG2101-1 | 29103-HTP-004 I/O-4-2 | 29103-HTP-004 |  | 113 | 29103-ET-PG2101-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2101-2-R-1 | 29103-ET-PG2101-2 | 29103-HTP-004 HTC-22 | 29103-HTP-004 |  | 113 | 29103-ET-PG2101-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2201-1-R-1 | 29103-ET-PG2201-1 | 29103-HTP-004 HTC-14 | 29103-HTP-004 |  | 113 | 29103-ET-PG2201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2201-1-R-2 | 29103-ET-PG2201-1 | 29103-HTP-004 I/O-4-1 | 29103-HTP-004 |  | 113 | 29103-ET-PG2201-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2201-2-R-1 | 29103-ET-PG2201-2 | 29103-HTP-004 HTC-17 | 29103-HTP-004 |  | 113 | 29103-ET-PG2201-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2301-1-R-1 | 29103-ET-PG2301-1 | 29103-HTP-004 HTC-11 | 29103-HTP-004 |  | 113 | 29103-ET-PG2301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2301-1-R-2 | 29103-ET-PG2301-1 | 29103-HTP-004 I/O-3-4 | 29103-HTP-004 |  | 113 | 29103-ET-PG2301-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2301-2-R-1 | 29103-ET-PG2301-2 | 29103-HTP-004 HTC-13 | 29103-HTP-004 |  | 113 | 29103-ET-PG2301-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2401-2-R-1 | 29103-ET-PG2401-2 | 29103-HTP-004 HTC-36 | 29103-HTP-004 |  | 113 | 29103-ET-PG2401-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-008 |  | 29103-HTP-004 HTC-16 | 29103-HTP-004 |  | 113 | 29103-RJB-008.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-009 |  | 29103-HTP-004 HTC-12 | 29103-HTP-004 |  | 113 | 29103-RJB-009.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-010 |  | 29103-HTP-004 HTC-07 | 29103-HTP-004 |  | 113 | 29103-RJB-010.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-011 |  | 29103-HTP-004 HTC-33 | 29103-HTP-004 |  | 113 | 29103-RJB-011.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup

## 29103-HTP-005
29103-HTP-005
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29103-ET-FG2401-1-1 | 29103-ET-FG2401-1 | 29103-AMB-009 | 29103-FG-2401 | 29103-65R-ET-FG2401-01-01 | 13.1 | 29103-ET-FG2401-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 23.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2401-1-2 | 29103-ET-FG2401-1 | 29103-AMB-009 |  | 29103-65R-ET-FG2401-01-01 | 13.1 | 29103-ET-FG2401-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 1.2 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2403-1-1 | 29103-ET-FG2403-1 | 29103-AMB-009 | 29103-FG-2403 | 29103-65R-ET-FG2403-01-01 | 13.1 | 29103-ET-FG2403-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 11.4 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2403-1-2 | 29103-ET-FG2403-1 | 29103-AMB-009 | 29103-FG-2403 | 29103-65R-ET-FG2403-01-01 | 13.1 | 29103-ET-FG2403-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 12.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2403-1-3 | 29103-ET-FG2403-1 | 29103-AMB-009 |  | 29103-65R-ET-FG2403-01-01 | 13.1 | 29103-ET-FG2403-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2403-1-4 | 29103-ET-FG2403-1 | 29103-AMB-009 |  | 29103-65R-ET-FG2403-01-01 | 13.1 | 29103-ET-FG2403-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2501-1-1 | 29103-ET-FG2501-1 | 29103-AMB-009 | 29103-FG-2501 | 29103-65R-ET-FG2501-01-01 | 13.1 | 29103-ET-FG2501-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 22.8 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2503-1-1 | 29103-ET-FG2503-1 | 29103-AMB-009 | 29103-FG-2503 | 29103-65R-ET-FG2503-01-01 | 13.1 | 29103-ET-FG2503-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 14 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2503-1-2 | 29103-ET-FG2503-1 | 29103-AMB-009 | 29103-FG-2503 | 29103-65R-ET-FG2503-01-01 | 13.1 | 29103-ET-FG2503-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 15.4 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2503-1-3 | 29103-ET-FG2503-1 | 29103-AMB-009 |  | 29103-65R-ET-FG2503-01-01 | 13.1 | 29103-ET-FG2503-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2503-1-4 | 29103-ET-FG2503-1 | 29103-AMB-009 |  | 29103-65R-ET-FG2503-01-01 | 13.1 | 29103-ET-FG2503-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2601-1-1 | 29103-ET-FG2601-1 | 29103-AMB-011 | 29103-FG-2601 | 29103-65R-ET-FG2601-01-01 | 13.1 | 29103-ET-FG2601-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 23.6 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2603-1-1 | 29103-ET-FG2603-1 | 29103-AMB-011 | 29103-FG-2603 | 29103-65R-ET-FG2603-01-01 | 13.1 | 29103-ET-FG2603-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 11.3 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2603-1-2 | 29103-ET-FG2603-1 | 29103-AMB-011 | 29103-FG-2603 | 29103-65R-ET-FG2603-01-01 | 13.1 | 29103-ET-FG2603-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 12.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2603-1-3 | 29103-ET-FG2603-1 | 29103-AMB-011 |  | 29103-65R-ET-FG2603-01-01 | 13.1 | 29103-ET-FG2603-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2603-1-4 | 29103-ET-FG2603-1 | 29103-AMB-011 |  | 29103-65R-ET-FG2603-01-01 | 13.1 | 29103-ET-FG2603-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2605-1-1 | 29103-ET-FG2605-1 | 29103-AMB-012 | 29103-FG-2606, 29103-FG-2605 | 29103-65R-ET-FG2605-01-01 | 13.1 | 29103-ET-FG2605-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 324.5 Ω | 2026-05-17 | [12 empty] | D/32SA2600/16M/243/277/1.2M/LS23A/X/N12 | 16 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2701-1-1 | 29103-ET-FG2701-1 | 29103-AMB-011 | 29103-FG-2701 | 29103-65R-ET-FG2701-01-01 | 13.1 | 29103-ET-FG2701-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 22.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2703-1-1 | 29103-ET-FG2703-1 | 29103-AMB-011 | 29103-FG-2703 | 29103-65R-ET-FG2703-01-01 | 13.1 | 29103-ET-FG2703-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2703-1-2 | 29103-ET-FG2703-1 | 29103-AMB-011 | 29103-FG-2703 | 29103-65R-ET-FG2703-01-01 | 13.1 | 29103-ET-FG2703-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 17.4 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2703-1-3 | 29103-ET-FG2703-1 | 29103-AMB-011 |  | 29103-65R-ET-FG2703-01-01 | 13.1 | 29103-ET-FG2703-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG2703-1-4 | 29103-ET-FG2703-1 | 29103-AMB-011 |  | 29103-65R-ET-FG2703-01-01 | 13.1 | 29103-ET-FG2703-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2401-1-1 | 29103-ET-P2401-1 | HTC-05 / CB-05 | 29103-P-2401 | 29103-65R-ET-P2401-01-01 | 13.1 | 29103-ET-P2401-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.6M/1001/165/1.2M/LS23A/X/N12/XNF | 20.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P2401-1-2 | 29103-ET-P2401-1 | HTC-05 / CB-05 | 29103-P-2401 | 29103-65R-ET-P2401-01-01 | 13.1 | 29103-ET-P2401-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.9M/676/112/1.2M/LS23A/X/N12/XMN | 13.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2501-1-1 | 29103-ET-P2501-1 | HTC-04 / CB-04 | 29103-P-2501 | 29103-65R-ET-P2501-01-01 | 13.1 | 29103-ET-P2501-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.5M/1007/166/1.2M/LS23A/X/N12/XNF | 20.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P2501-1-2 | 29103-ET-P2501-1 | HTC-04 / CB-04 | 29103-P-2501 | 29103-65R-ET-P2501-01-01 | 13.1 | 29103-ET-P2501-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.8M/678/111/1.2M/LS23A/X/N12/XMN | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2504-1-1 | 29103-ET-P2504-1 | HTC-09 / CB-09 | 29103-PE-2501, 29103-P-2504 | 29103-65R-ET-P2504-01-01 | 13.1 | 29103-ET-P2504-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2504-1-2 | 29103-ET-P2504-1 | HTC-09 / CB-09 | 29103-P-2504 | 29103-65R-ET-P2504-01-01 | 13.1 | 29103-ET-P2504-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.7 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/8M/461/78.9/1.2M/LS23A/X/N12/XNF | 8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2504-1-3 | 29103-ET-P2504-1 | HTC-09 / CB-09 | 29103-P-2504 | 29103-65R-ET-P2504-01-01 | 13.1 | 29103-ET-P2504-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/403/69/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2504-1-4 | 29103-ET-P2504-1 | HTC-09 / CB-09 | 29103-P-2504 | 29103-65R-ET-P2504-01-01 | 13.1 | 29103-ET-P2504-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/755/129/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2504-2-1 | 29103-ET-P2504-2 | HTC-20 / CB-20 | 29103-P-2504, 29103-FG-2502 | 29103-65R-ET-P2504-02-01 | 13.1 | 29103-ET-P2504-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 371.4 Ω | 2026-05-17 | [12 empty] | D/32SF1180/6.2M/207/277/1.2M/LS23A/X/N12 | 6.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P2601-1-1 | 29103-ET-P2601-1 | HTC-35 / CB-35 | 29103-P-2601 | 29103-65R-ET-P2601-01-01 | 13.1 | 29103-ET-P2601-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.6M/1001/165/1.2M/LS23A/X/N12/XNF | 20.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P2601-1-2 | 29103-ET-P2601-1 | HTC-35 / CB-35 | 29103-P-2601 | 29103-65R-ET-P2601-01-01 | 13.1 | 29103-ET-P2601-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.9M/676/112/1.2M/LS23A/X/N12/XMN | 13.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2604-1-1 | 29103-ET-P2604-1 | HTC-32 / CB-32 | 29103-PE-2601, 29103-P-2604 | 29103-65R-ET-P2604-01-01 | 13.1 | 29103-ET-P2604-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2604-1-2 | 29103-ET-P2604-1 | HTC-32 / CB-32 | 29103-P-2604 | 29103-65R-ET-P2604-01-01 | 13.1 | 29103-ET-P2604-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 10.5 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/6.5M/416/67.7/1.2M/LS23A/X/N12/XNF | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P2604-1-3 | 29103-ET-P2604-1 | HTC-32 / CB-32 | 29103-P-2604 | 29103-65R-ET-P2604-01-01 | 13.1 | 29103-ET-P2604-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.3 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/448/72.9/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2604-1-4 | 29103-ET-P2604-1 | HTC-32 / CB-32 | 29103-P-2604 | 29103-65R-ET-P2604-01-01 | 13.1 | 29103-ET-P2604-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/838/136/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2604-2-1 | 29103-ET-P2604-2 | HTC-24 / CB-24 | 29103-P-2604, 29103-FG-2602 | 29103-65R-ET-P2604-02-01 | 13.1 | 29103-ET-P2604-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 262.4 Ω | 2026-05-17 | [12 empty] | D/32SF1110/7M/299/277/1.2M/LS23A/X/N12 | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2701-1-1 | 29103-ET-P2701-1 | HTC-22 / CB-22 | 29103-P-2701 | 29103-65R-ET-P2701-01-01 | 13.1 | 29103-ET-P2701-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.5M/1007/166/1.2M/LS23A/X/N12/XNF | 20.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P2701-1-2 | 29103-ET-P2701-1 | HTC-22 / CB-22 | 29103-P-2701 | 29103-65R-ET-P2701-01-01 | 13.1 | 29103-ET-P2701-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.8M/678/111/1.2M/LS23A/X/N12/XMN | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2704-1-1 | 29103-ET-P2704-1 | HTC-29 / CB-29 | 29103-PE-2701, 29103-P-2704 | 29103-65R-ET-P2704-01-01 | 13.1 | 29103-ET-P2704-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P2704-1-2 | 29103-ET-P2704-1 | HTC-29 / CB-29 | 29103-P-2704 | 29103-65R-ET-P2704-01-01 | 13.1 | 29103-ET-P2704-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.8 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/8M/461/78.9/1.2M/LS23A/X/N12/XNF | 8 m m | Levy Ostrup
EHT Trace | 29103-ET-P2704-1-3 | 29103-ET-P2704-1 | HTC-29 / CB-29 | 29103-P-2704 | 29103-65R-ET-P2704-01-01 | 13.1 | 29103-ET-P2704-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.3 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/403/69/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P2704-1-4 | 29103-ET-P2704-1 | HTC-29 / CB-29 | 29103-P-2704 | 29103-65R-ET-P2704-01-01 | 13.1 | 29103-ET-P2704-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/755/129/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P2704-2-1 | 29103-ET-P2704-2 | HTC-27 / CB-27 | 29103-P-2704, 29103-FG-2702 | 29103-65R-ET-P2704-02-01 | 13.1 | 29103-ET-P2704-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 368 Ω | 2026-05-17 | [12 empty] | D/32SF1180/6.2M/207/277/1.2M/LS23A/X/N12 | 6.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-1-1 | 29103-ET-P2800-1 | HTC-17 / CB-17 | 29103-P-2800 | 29103-65R-ET-P2800-01-01 | 13.1 | 29103-ET-P2800-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/58.6M/2332/198/2.1M/LS23A/X/N12 | 58.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P2800-1-2 | 29103-ET-P2800-1 | HTC-17 / CB-17 | 29103-P-2800 | 29103-65R-ET-P2800-01-01 | 13.1 | 29103-ET-P2800-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/23.3M/927/78.8/2.1M/LS23A/X/N12 | 23.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2401-1-1 | 29103-ET-PE2401-1 | HTC-08 / CB-08 | 29103-PE-2401 | 29103-65R-ET-PE2401-01-01 | 13.1 | 29103-ET-PE2401-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.5M/280/277/1.2M/LS23A/X/N12 | 7.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2401-1-2 | 29103-ET-PE2401-1 | HTC-08 / CB-08 | 29103-PE-2401 | 29103-65R-ET-PE2401-01-01 | 13.1 | 29103-ET-PE2401-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/10.8M/522/97.1/1.2M/LS23A/X/N12/XNF | 10.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2401-1-3 | 29103-ET-PE2401-1 | HTC-08 / CB-08 | 29103-PE-2401 | 29103-65R-ET-PE2401-01-01 | 13.1 | 29103-ET-PE2401-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/319/59.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2401-1-4 | 29103-ET-PE2401-1 | HTC-08 / CB-08 | 29103-PE-2401 | 29103-65R-ET-PE2401-01-01 | 13.1 | 29103-ET-PE2401-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.4M/647/121/1.2M/LS23A/X/N12/XMN | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2501-1-1 | 29103-ET-PE2501-1 | HTC-10 / CB-10 | 29103-PE-2501 | 29103-65R-ET-PE2501-01-01 | 13.1 | 29103-ET-PE2501-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.8M/269/277/1.2M/LS23A/X/N12 | 7.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2501-1-2 | 29103-ET-PE2501-1 | HTC-10 / CB-10 | 29103-PE-2501 | 29103-65R-ET-PE2501-01-01 | 13.1 | 29103-ET-PE2501-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/9.5M/505/89.8/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2501-1-3 | 29103-ET-PE2501-1 | HTC-10 / CB-10 | 29103-PE-2501 | 29103-65R-ET-PE2501-01-01 | 13.1 | 29103-ET-PE2501-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/351/62.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2501-1-4 | 29103-ET-PE2501-1 | HTC-10 / CB-10 | 29103-PE-2501 | 29103-65R-ET-PE2501-01-01 | 13.1 | 29103-ET-PE2501-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.2M/702/125/1.2M/LS23A/X/N12/XMN | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2501-2-1 | 29103-ET-PE2501-2 | HTC-07 / CB-07 | 29103-PE-2501 | 29103-65R-ET-PE2501-02-01 | 13.1 | 29103-ET-PE2501-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.5M/2063/277/1.2M/LS23A/X/N12 | 52.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2501-2-2 | 29103-ET-PE2501-2 | HTC-07 / CB-07 | 29103-PE-2501 | 29103-65R-ET-PE2501-02-01 | 13.1 | 29103-ET-PE2501-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.4M/694/277/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2502-1-1 | 29103-ET-PE2502-1 | HTC-06 / CB-06 | 29103-PE-2503, 29103-PE-2502 | 29103-65R-ET-PE2502-01-01 | 13.1 | 29103-ET-PE2502-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/34.9M/1658/277/1.2M/LS23A/X/N12 | 34.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2601-1-1 | 29103-ET-PE2601-1 | HTC-31 / CB-31 | 29103-PE-2601 | 29103-65R-ET-PE2601-01-01 | 13.1 | 29103-ET-PE2601-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.5M/280/277/1.2M/LS23A/X/N12 | 7.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2601-1-2 | 29103-ET-PE2601-1 | HTC-31 / CB-31 | 29103-PE-2601 | 29103-65R-ET-PE2601-01-01 | 13.1 | 29103-ET-PE2601-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/10.8M/522/97.1/1.2M/LS23A/X/N12/XNF | 10.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2601-1-3 | 29103-ET-PE2601-1 | HTC-31 / CB-31 | 29103-PE-2601 | 29103-65R-ET-PE2601-01-01 | 13.1 | 29103-ET-PE2601-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/319/59.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2601-1-4 | 29103-ET-PE2601-1 | HTC-31 / CB-31 | 29103-PE-2601 | 29103-65R-ET-PE2601-01-01 | 13.1 | 29103-ET-PE2601-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.4M/647/121/1.2M/LS23A/X/N12/XMN | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2601-2-1 | 29103-ET-PE2601-2 | HTC-12 / CB-12 | 29103-PE-2601 | 29103-65R-ET-PE2601-02-01 | 13.1 | 29103-ET-PE2601-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.1M/2079/277/1.2M/LS23A/X/N12 | 52.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2601-2-2 | 29103-ET-PE2601-2 | HTC-12 / CB-12 | 29103-PE-2601 | 29103-65R-ET-PE2601-02-01 | 13.1 | 29103-ET-PE2601-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.2M/701/277/1.2M/LS23A/X/N12 | 29.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2602-1-1 | 29103-ET-PE2602-1 | HTC-25 / CB-25 | 29103-PE-2603, 29103-PE-2602 | 29103-65R-ET-PE2602-01-01 | 13.1 | 29103-ET-PE2602-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/35.4M/1635/277/1.2M/LS23A/X/N12 | 35.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2701-1-1 | 29103-ET-PE2701-1 | HTC-33 / CB-33 | 29103-PE-2701 | 29103-65R-ET-PE2701-01-01 | 13.1 | 29103-ET-PE2701-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.8M/269/277/1.2M/LS23A/X/N12 | 7.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2701-1-2 | 29103-ET-PE2701-1 | HTC-33 / CB-33 | 29103-PE-2701 | 29103-65R-ET-PE2701-01-01 | 13.1 | 29103-ET-PE2701-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/9.5M/505/89.8/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2701-1-3 | 29103-ET-PE2701-1 | HTC-33 / CB-33 | 29103-PE-2701 | 29103-65R-ET-PE2701-01-01 | 13.1 | 29103-ET-PE2701-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/351/62.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2701-1-4 | 29103-ET-PE2701-1 | HTC-33 / CB-33 | 29103-PE-2701 | 29103-65R-ET-PE2701-01-01 | 13.1 | 29103-ET-PE2701-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.2M/702/125/1.2M/LS23A/X/N12/XMN | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2701-2-1 | 29103-ET-PE2701-2 | HTC-03 / CB-03 | 29103-PE-2701 | 29103-65R-ET-PE2701-02-01 | 13.1 | 29103-ET-PE2701-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.5M/2063/277/1.2M/LS23A/X/N12 | 52.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2701-2-2 | 29103-ET-PE2701-2 | HTC-03 / CB-03 | 29103-PE-2701 | 29103-65R-ET-PE2701-02-01 | 13.1 | 29103-ET-PE2701-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.4M/694/277/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2702-1-1 | 29103-ET-PE2702-1 | HTC-26 / CB-26 | 29103-PE-2703, 29103-PE-2702 | 29103-65R-ET-PE2702-01-01 | 13.1 | 29103-ET-PE2702-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/34.9M/1658/277/1.2M/LS23A/X/N12 | 34.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-1-1 | 29103-ET-PE2802-1 | HTC-02 / CB-02 | 29103-PE-2802 | 29103-65R-ET-PE2802-01-01 | 13.1 | 29103-ET-PE2802-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SP4734/24.2M/2105/126/2.1-1.2M/LS23A/X/N12/XNF | 24.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-1-2 | 29103-ET-PE2802-1 | HTC-02 / CB-02 | 29103-PE-2802 | 29103-65R-ET-PE2802-01-01 | 13.1 | 29103-ET-PE2802-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SP4734/8.9M/774/46.2/1.2M/LS23A/X/N12/XMF | 8.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-1-3 | 29103-ET-PE2802-1 | HTC-02 / CB-02 | 29103-PE-2802 | 29103-65R-ET-PE2802-01-01 | 13.1 | 29103-ET-PE2802-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/20.3M/1766/105/1.2M/LS23A/X/N12/XMN | 20.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-2-1 | 29103-ET-PE2802-2 | HTC-18 / CB-18 | 29103-PE-2802 | 29103-65R-ET-PE2802-02-01 | 13.1 | 29103-ET-PE2802-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3150/8.8M/784/61.6/2.1-1.2M/LS23A/X/N12/XNF | 8.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-2-2 | 29103-ET-PE2802-2 | HTC-18 / CB-18 | 29103-PE-2802 | 29103-65R-ET-PE2802-02-01 | 13.1 | 29103-ET-PE2802-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3150/21.6M/1925/151/1.2M/LS23A/X/N12/XMF | 21.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2802-2-3 | 29103-ET-PE2802-2 | HTC-18 / CB-18 | 29103-PE-2802 | 29103-65R-ET-PE2802-02-01 | 13.1 | 29103-ET-PE2802-2-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3150/9.2M/820/64.4/1.2M/LS23A/X/N12/XMN | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2803-1-1 | 29103-ET-PE2803-1 | HTC-21 / CB-21 | 29103-PE-2803 | 29103-65R-ET-PE2803-01-01 | 13.1 | 29103-ET-PE2803-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3100/9.7M/437/38.8/1.2M/LS23A/X/N12/XNF | 9.7 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2803-1-2 | 29103-ET-PE2803-1 | HTC-21 / CB-21 | 29103-PE-2803 | 29103-65R-ET-PE2803-01-01 | 13.1 | 29103-ET-PE2803-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/26.3M/1186/105/1.2M/LS23A/X/N12/XMN | 26.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2803-1-3 | 29103-ET-PE2803-1 | HTC-21 / CB-21 | 29103-PE-2803 | 29103-65R-ET-PE2803-01-01 | 13.1 | 29103-ET-PE2803-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3100/22.1M/997/88.3/1.2M/LS23A/X/N12/XNF | 22.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE2803-1-4 | 29103-ET-PE2803-1 | HTC-21 / CB-21 | 29103-PE-2803 | 29103-65R-ET-PE2803-01-01 | 13.1 | 29103-ET-PE2803-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/11.2M/505/44.8/1.2M/LS23A/X/N12/XMN | 11.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2401-1-1 | 29103-ET-PG2401-1 | HTC-14 / CB-14 | 29103-PG-2401, 29103-PE-2402, 29103-P-2400 | 29103-65R-ET-PG2401-01-01 | 13.1 | 29103-ET-PG2401-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/93.1M/2914/277/1.2M/LS23A/X/N12 | 93.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2501-1-1 | 29103-ET-PG2501-1 | HTC-11 / CB-11 | 29103-PG-2501, 29103-PE-2502, 29103-P-2500 | 29103-65R-ET-PG2501-01-01 | 13.1 | 29103-ET-PG2501-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/89M/3035/277/1.2M/LS23A/X/N12 | 89 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2501-2-1 | 29103-ET-PG2501-2 | HTC-13 / CB-13 | 29103-PG-2501 | 29103-65R-ET-PG2501-02-01 | 13.1 | 29103-ET-PG2501-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 21.7 Ω | 2026-05-18 | [12 empty] | E/32SB3700/9.2M/409/93.3/1.2M/LS23A/X/N12/XNF | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2501-2-2 | 29103-ET-PG2501-2 | HTC-13 / CB-13 | 29103-PG-2501 | 29103-65R-ET-PG2501-02-01 | 13.1 | 29103-ET-PG2501-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 14.9 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/280/63.9/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2501-2-3 | 29103-ET-PG2501-2 | HTC-13 / CB-13 | 29103-PG-2501 | 29103-65R-ET-PG2501-02-01 | 13.1 | 29103-ET-PG2501-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28.1 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/525/120/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2601-1-1 | 29103-ET-PG2601-1 | HTC-28 / CB-28 | 29103-PG-2601, 29103-PE-2602, 29103-P-2600 | 29103-65R-ET-PG2601-01-01 | 13.1 | 29103-ET-PG2601-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/93.1M/2914/277/1.2M/LS23A/X/N12 | 93.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2601-2-1 | 29103-ET-PG2601-2 | HTC-19 / CB-19 | 29103-PG-2601 | 29103-65R-ET-PG2601-02-01 | 13.1 | 29103-ET-PG2601-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 20.3 Ω | 2026-05-18 | [12 empty] | E/32SB3700/8.6M/401/89.2/1.2M/LS23A/X/N12/XNF | 8.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2601-2-2 | 29103-ET-PG2601-2 | HTC-19 / CB-19 | 29103-PG-2601 | 29103-65R-ET-PG2601-02-01 | 13.1 | 29103-ET-PG2601-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 14.9 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/294/65.4/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2601-2-3 | 29103-ET-PG2601-2 | HTC-19 / CB-19 | 29103-PG-2601 | 29103-65R-ET-PG2601-02-01 | 13.1 | 29103-ET-PG2601-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/550/122/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2701-1-1 | 29103-ET-PG2701-1 | HTC-23 / CB-23 | 29103-PG-2701, 29103-PE-2702, 29103-P-2700 | 29103-65R-ET-PG2701-01-01 | 13.1 | 29103-ET-PG2701-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/90M/3006/277/1.2M/LS23A/X/N12 | 90 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2701-2-1 | 29103-ET-PG2701-2 | HTC-30 / CB-30 | 29103-PG-2701 | 29103-65R-ET-PG2701-02-01 | 13.1 | 29103-ET-PG2701-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 21.6 Ω | 2026-05-18 | [12 empty] | E/32SB3700/9.2M/409/93.3/1.2M/LS23A/X/N12/XNF | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2701-2-2 | 29103-ET-PG2701-2 | HTC-30 / CB-30 | 29103-PG-2701 | 29103-65R-ET-PG2701-02-01 | 13.1 | 29103-ET-PG2701-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 15 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/280/63.9/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG2701-2-3 | 29103-ET-PG2701-2 | HTC-30 / CB-30 | 29103-PG-2701 | 29103-65R-ET-PG2701-02-01 | 13.1 | 29103-ET-PG2701-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28.1 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/525/120/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-SC2800-1-1 | 29103-ET-SC2800-1 | 29103-AMB-012 | 29103-ST-2815, 29103-ST-2814, 29103-ST-2813, 29103- ST-2812, 29103-SC-2802, 29103-SC-2800 | 29103-65R-ET-SC2800-01-01 | 13.1 | 29103-ET-SC2800-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3914/39.4M/650/277/1.2M/LS23A/X/N12 | 39.4 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2001-1-1 | 29103-ET-ST2001-1 | 29103-AMB-012 | 29103-ST-2001 | 29103-65R-ET-ST2001-01-01 | 13.1 | 29103-ET-ST2001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/12.6M/169/89.3/1.2M/LS23A/X/N12/XNF | 12.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2001-1-2 | 29103-ET-ST2001-1 | 29103-AMB-012 | 29103-ST-2002, 29103-ST-2001 | 29103-65R-ET-ST2001-01-01 | 13.1 | 29103-ET-ST2001-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/26.5M/355/188/1.2M/LS23A/X/N12/XMN | 26.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2603-1-1 | 29103-ET-ST2603-1 | 29103-AMB-012 | 29103-ST-2604, 29103-ST-2603 | 29103-65R-ET-ST2603-01-01 | 13.1 | 29103-ET-ST2603-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.3M/282/135/1.2M/LS23A/X/N12/XNF | 17.3 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2603-1-2 | 29103-ET-ST2603-1 | 29103-AMB-012 | 29103-ST-2604 | 29103-65R-ET-ST2603-01-01 | 13.1 | 29103-ET-ST2603-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/297/142/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2603-1-3 | 29103-ET-ST2603-1 | 29103-AMB-012 | 29103-ST-2603 | 29103-65R-ET-ST2603-01-01 | 13.1 | 29103-ET-ST2603-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 51.9 Ω | 2026-05-18 | [12 empty] | E/32SA2200/7.6M/127/79.7/1.2M/LS23A/X/N12/XNF | 7.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2603-1-4 | 29103-ET-ST2603-1 | 29103-AMB-012 | 29103-ST-2603 | 29103-65R-ET-ST2603-01-01 | 13.1 | 29103-ET-ST2603-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 38.6 Ω | 2026-05-18 | [12 empty] | E/32SA2200/5.7M/95/59.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2603-1-5 | 29103-ET-ST2603-1 | 29103-AMB-012 | 29103-ST-2603 | 29103-65R-ET-ST2603-01-01 | 13.1 | 29103-ET-ST2603-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 87.9 Ω | 2026-05-18 | [12 empty] | D/32SA2200/13.1M/219/137/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2703-1-1 | 29103-ET-ST2703-1 | 29103-AMB-012 | 29103-ST-2704, 29103-ST-2703 | 29103-65R-ET-ST2703-01-01 | 13.1 | 29103-ET-ST2703-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.5M/282/136/1.2M/LS23A/X/N12/XNF | 17.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2703-1-2 | 29103-ET-ST2703-1 | 29103-AMB-012 | 29103-ST-2704 | 29103-65R-ET-ST2703-01-01 | 13.1 | 29103-ET-ST2703-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/293/141/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2703-1-3 | 29103-ET-ST2703-1 | 29103-AMB-012 | 29103-ST-2703 | 29103-65R-ET-ST2703-01-01 | 13.1 | 29103-ET-ST2703-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 55.3 Ω | 2026-05-18 | [12 empty] | E/32SA2170/9.5M/162/93/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2703-1-4 | 29103-ET-ST2703-1 | 29103-AMB-012 | 29103-ST-2703 | 29103-65R-ET-ST2703-01-01 | 13.1 | 29103-ET-ST2703-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 33 Ω | 2026-05-18 | [12 empty] | E/32SA2170/5.7M/97/55.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST2703-1-5 | 29103-ET-ST2703-1 | 29103-AMB-012 | 29103-ST-2703 | 29103-65R-ET-ST2703-01-01 | 13.1 | 29103-ET-ST2703-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 76 Ω | 2026-05-18 | [12 empty] | D/32SA2170/13.1M/224/128/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
Power Cable | 29103-AMB-009 |  | 29103-HTP-005 HTC-01 | 29103-HTP-005 |  | 113 | 29103-AMB-009.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-011 |  | 29103-HTP-005 HTC-15 | 29103-HTP-005 |  | 113 | 29103-AMB-011.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-012 |  | 29103-HTP-005 HTC-16 | 29103-HTP-005 |  | 113 | 29103-AMB-012.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-FG2401-1-PWK-1 | 29103-ET-FG2401-1 | 29103-AMB-009 | 29103-HTP-005 |  | 113 | 29103-ET-FG2401-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2403-1-PWK-1 | 29103-ET-FG2403-1 | 29103-AMB-009 | 29103-HTP-005 |  | 113 | 29103-ET-FG2403-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2501-1-PWK-1 | 29103-ET-FG2501-1 | 29103-AMB-009 | 29103-HTP-005 |  | 113 | 29103-ET-FG2501-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2503-1-PWK-1 | 29103-ET-FG2503-1 | 29103-AMB-009 | 29103-HTP-005 |  | 113 | 29103-ET-FG2503-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2601-1-PWK-1 | 29103-ET-FG2601-1 | 29103-AMB-011 | 29103-HTP-005 |  | 113 | 29103-ET-FG2601-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2603-1-PWK-1 | 29103-ET-FG2603-1 | 29103-AMB-011 | 29103-HTP-005 |  | 113 | 29103-ET-FG2603-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2605-1-PWK-1 | 29103-ET-FG2605-1 | 29103-AMB-012 | 29103-HTP-005 |  | 113 | 29103-ET-FG2605-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2701-1-PWK-1 | 29103-ET-FG2701-1 | 29103-AMB-011 | 29103-HTP-005 |  | 113 | 29103-ET-FG2701-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG2703-1-PWK-1 | 29103-ET-FG2703-1 | 29103-AMB-011 | 29103-HTP-005 |  | 113 | 29103-ET-FG2703-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2401-1-PWK-1 | 29103-ET-P2401-1 | 29103-HTP-005 HTC-05 | 29103-HTP-005 |  | 113 | 29103-ET-P2401-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2501-1-PWK-1 | 29103-ET-P2501-1 | 29103-HTP-005 HTC-04 | 29103-HTP-005 |  | 113 | 29103-ET-P2501-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2504-1-PWK-1 | 29103-ET-P2504-1 | 29103-HTP-005 HTC-09 | 29103-HTP-005 |  | 113 | 29103-ET-P2504-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2504-2-PWK-1 | 29103-ET-P2504-2 | 29103-HTP-005 HTC-20 | 29103-HTP-005 |  | 113 | 29103-ET-P2504-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2601-1-PWK-1 | 29103-ET-P2601-1 | 29103-HTP-005 HTC-35 | 29103-HTP-005 |  | 113 | 29103-ET-P2601-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2604-1-PWK-1 | 29103-ET-P2604-1 | 29103-HTP-005 HTC-32 | 29103-HTP-005 |  | 113 | 29103-ET-P2604-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2604-2-PWK-1 | 29103-ET-P2604-2 | 29103-HTP-005 HTC-24 | 29103-HTP-005 |  | 113 | 29103-ET-P2604-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2701-1-PWK-1 | 29103-ET-P2701-1 | 29103-HTP-005 HTC-22 | 29103-HTP-005 |  | 113 | 29103-ET-P2701-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2704-1-PWK-1 | 29103-ET-P2704-1 | 29103-HTP-005 HTC-29 | 29103-HTP-005 |  | 113 | 29103-ET-P2704-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2704-2-PWK-1 | 29103-ET-P2704-2 | 29103-HTP-005 HTC-27 | 29103-HTP-005 |  | 113 | 29103-ET-P2704-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P2800-1-PWK-1 | 29103-ET-P2800-1 | 29103-HTP-005 HTC-17 | 29103-HTP-005 |  | 113 | 29103-ET-P2800-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2401-1-PWK-1 | 29103-ET-PE2401-1 | 29103-HTP-005 HTC-08 | 29103-HTP-005 |  | 113 | 29103-ET-PE2401-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2501-1-PWK-1 | 29103-ET-PE2501-1 | 29103-HTP-005 HTC-10 | 29103-HTP-005 |  | 113 | 29103-ET-PE2501-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2501-2-PWK-1 | 29103-ET-PE2501-2 | 29103-HTP-005 HTC-07 | 29103-HTP-005 |  | 113 | 29103-ET-PE2501-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2502-1-PWK-1 | 29103-ET-PE2502-1 | 29103-HTP-005 HTC-06 | 29103-HTP-005 |  | 113 | 29103-ET-PE2502-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2601-1-PWK-1 | 29103-ET-PE2601-1 | 29103-HTP-005 HTC-31 | 29103-HTP-005 |  | 113 | 29103-ET-PE2601-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2601-2-PWK-1 | 29103-ET-PE2601-2 | 29103-HTP-005 HTC-12 | 29103-HTP-005 |  | 113 | 29103-ET-PE2601-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2602-1-PWK-1 | 29103-ET-PE2602-1 | 29103-HTP-005 HTC-25 | 29103-HTP-005 |  | 113 | 29103-ET-PE2602-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2701-1-PWK-1 | 29103-ET-PE2701-1 | 29103-HTP-005 HTC-33 | 29103-HTP-005 |  | 113 | 29103-ET-PE2701-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2701-2-PWK-1 | 29103-ET-PE2701-2 | 29103-HTP-005 HTC-03 | 29103-HTP-005 |  | 113 | 29103-ET-PE2701-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2702-1-PWK-1 | 29103-ET-PE2702-1 | 29103-HTP-005 HTC-26 | 29103-HTP-005 |  | 113 | 29103-ET-PE2702-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2802-1-PWK-1 | 29103-ET-PE2802-1 | 29103-HTP-005 HTC-02 | 29103-HTP-005 |  | 113 | 29103-ET-PE2802-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2802-2-PWK-1 | 29103-ET-PE2802-2 | 29103-HTP-005 HTC-18 | 29103-HTP-005 |  | 113 | 29103-ET-PE2802-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE2803-1-PWK-1 | 29103-ET-PE2803-1 | 29103-HTP-005 HTC-21 | 29103-HTP-005 |  | 113 | 29103-ET-PE2803-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2401-1-PWK-1 | 29103-ET-PG2401-1 | 29103-HTP-005 HTC-14 | 29103-HTP-005 |  | 113 | 29103-ET-PG2401-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2501-1-PWK-1 | 29103-ET-PG2501-1 | 29103-HTP-005 HTC-11 | 29103-HTP-005 |  | 113 | 29103-ET-PG2501-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2501-2-PWK-1 | 29103-ET-PG2501-2 | 29103-HTP-005 HTC-13 | 29103-HTP-005 |  | 113 | 29103-ET-PG2501-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2601-1-PWK-1 | 29103-ET-PG2601-1 | 29103-HTP-005 HTC-28 | 29103-HTP-005 |  | 113 | 29103-ET-PG2601-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2601-2-PWK-1 | 29103-ET-PG2601-2 | 29103-HTP-005 HTC-19 | 29103-HTP-005 |  | 113 | 29103-ET-PG2601-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2701-1-PWK-1 | 29103-ET-PG2701-1 | 29103-HTP-005 HTC-23 | 29103-HTP-005 |  | 113 | 29103-ET-PG2701-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG2701-2-PWK-1 | 29103-ET-PG2701-2 | 29103-HTP-005 HTC-30 | 29103-HTP-005 |  | 113 | 29103-ET-PG2701-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-SC2800-1-PWK-1 | 29103-ET-SC2800-1 | 29103-AMB-012 | 29103-HTP-005 |  | 113 | 29103-ET-SC2800-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2001-1-PWK-1 | 29103-ET-ST2001-1 | 29103-AMB-012 | 29103-HTP-005 |  | 113 | 29103-ET-ST2001-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2603-1-PWK-1 | 29103-ET-ST2603-1 | 29103-AMB-012 | 29103-HTP-005 |  | 113 | 29103-ET-ST2603-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST2703-1-PWK-1 | 29103-ET-ST2703-1 | 29103-AMB-012 | 29103-HTP-005 |  | 113 | 29103-ET-ST2703-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
RTD | 29103-ET-P2401-1-R-1 | 29103-ET-P2401-1 | 29103-HTP-005 HTC-05 | PRODUCED EMULSION | 29103-65R-ET-P2401-01-01 | 13.2 | 29103-ET-P2401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2501-1-R-1 | 29103-ET-P2501-1 | 29103-HTP-005 HTC-04 | PRODUCED EMULSION | 29103-65R-ET-P2501-01-01 | 13.2 | 29103-ET-P2501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2504-1-R-1 | 29103-ET-P2504-1 | 29103-HTP-005 HTC-09 | PRODUCED EMULSION | 29103-65R-ET-P2504-01-01 | 13.2 | 29103-ET-P2504-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2504-1-R-2 | 29103-ET-P2504-1 | 29103-HTP-005 I/O-1-4 | PRODUCED EMULSION | 29103-65R-ET-P2504-01-01 | 13.2 | 29103-ET-P2504-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2504-2-R-1 | 29103-ET-P2504-2 | 29103-HTP-005 HTC-20 | PRODUCED EMULSION | 29103-65R-ET-P2504-02-01 | 13.2 | 29103-ET-P2504-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2504-2-R-2 | 29103-ET-P2504-2 | 29103-HTP-005 I/O-3-4 | PRODUCED EMULSION | 29103-65R-ET-P2504-02-01 | 13.2 | 29103-ET-P2504-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2601-1-R-1 | 29103-ET-P2601-1 | 29103-HTP-005 HTC-35 | PRODUCED EMULSION | 29103-65R-ET-P2601-01-01 | 13.2 | 29103-ET-P2601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2604-1-R-1 | 29103-ET-P2604-1 | 29103-HTP-005 HTC-32 | PRODUCED EMULSION | 29103-65R-ET-P2604-01-01 | 13.2 | 29103-ET-P2604-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2604-1-R-2 | 29103-ET-P2604-1 | 29103-HTP-005 I/O-2-1 | PRODUCED EMULSION | 29103-65R-ET-P2604-01-01 | 13.2 | 29103-ET-P2604-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2604-2-R-1 | 29103-ET-P2604-2 | 29103-HTP-005 HTC-24 | PRODUCED EMULSION | 29103-65R-ET-P2604-02-01 | 13.2 | 29103-ET-P2604-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2604-2-R-2 | 29103-ET-P2604-2 | 29103-HTP-005 I/O-2-2 | PRODUCED EMULSION | 29103-65R-ET-P2604-02-01 | 13.2 | 29103-ET-P2604-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2701-1-R-1 | 29103-ET-P2701-1 | 29103-HTP-005 HTC-22 | PRODUCED EMULSION | 29103-65R-ET-P2701-01-01 | 13.2 | 29103-ET-P2701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2704-1-R-1 | 29103-ET-P2704-1 | 29103-HTP-005 HTC-29 | PRODUCED EMULSION | 29103-65R-ET-P2704-01-01 | 13.2 | 29103-ET-P2704-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2704-1-R-2 | 29103-ET-P2704-1 | 29103-HTP-005 I/O-4-2 | PRODUCED EMULSION | 29103-65R-ET-P2704-01-01 | 13.2 | 29103-ET-P2704-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2704-2-R-1 | 29103-ET-P2704-2 | 29103-HTP-005 HTC-27 | PRODUCED EMULSION | 29103-65R-ET-P2704-02-01 | 13.2 | 29103-ET-P2704-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2704-2-R-2 | 29103-ET-P2704-2 | 29103-HTP-005 I/O-4-3 | PRODUCED EMULSION | 29103-65R-ET-P2704-02-01 | 13.2 | 29103-ET-P2704-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P2800-1-R-1 | 29103-ET-P2800-1 | 29103-HTP-005 HTC-17 | PRODUCED EMULSION | 29103-65R-ET-P2800-01-01 | 13.2 | 29103-ET-P2800-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2401-1-R-1 | 29103-ET-PE2401-1 | 29103-HTP-005 HTC-08 | PRODUCED EMULSION | 29103-65R-ET-PE2401-01-01 | 13.2 | 29103-ET-PE2401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2501-1-R-1 | 29103-ET-PE2501-1 | 29103-HTP-005 HTC-10 | PRODUCED EMULSION | 29103-65R-ET-PE2501-01-01 | 13.2 | 29103-ET-PE2501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2501-2-R-2 | 29103-ET-PE2501-2 | 29103-HTP-005 I/O-2-3 | PRODUCED EMULSION | 29103-65R-ET-PE2501-02-01 | 13.2 | 29103-ET-PE2501-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2502-1-R-1 | 29103-ET-PE2502-1 | 29103-HTP-005 HTC-06 | PRODUCED EMULSION | 29103-65R-ET-PE2502-01-01 | 13.2 | 29103-ET-PE2502-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2502-1-R-2 | 29103-ET-PE2502-1 | 29103-HTP-005 I/O-2-4 | PRODUCED EMULSION | 29103-65R-ET-PE2502-01-01 | 13.2 | 29103-ET-PE2502-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2601-1-R-1 | 29103-ET-PE2601-1 | 29103-HTP-005 HTC-31 | PRODUCED EMULSION | 29103-65R-ET-PE2601-01-01 | 13.2 | 29103-ET-PE2601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2601-2-R-2 | 29103-ET-PE2601-2 | 29103-HTP-005 I/O-1-3 | PRODUCED EMULSION | 29103-65R-ET-PE2601-02-01 | 13.2 | 29103-ET-PE2601-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2602-1-R-1 | 29103-ET-PE2602-1 | 29103-HTP-005 HTC-25 | PRODUCED EMULSION | 29103-65R-ET-PE2602-01-01 | 13.2 | 29103-ET-PE2602-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2602-1-R-2 | 29103-ET-PE2602-1 | 29103-HTP-005 I/O-3-3 | PRODUCED EMULSION | 29103-65R-ET-PE2602-01-01 | 13.2 | 29103-ET-PE2602-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2701-1-R-1 | 29103-ET-PE2701-1 | 29103-HTP-005 HTC-33 | PRODUCED EMULSION | 29103-65R-ET-PE2701-01-01 | 13.2 | 29103-ET-PE2701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2701-2-R-2 | 29103-ET-PE2701-2 | 29103-HTP-005 I/O-4-4 | PRODUCED EMULSION | 29103-65R-ET-PE2701-02-01 | 13.2 | 29103-ET-PE2701-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2702-1-R-1 | 29103-ET-PE2702-1 | 29103-HTP-005 HTC-26 | PRODUCED EMULSION | 29103-65R-ET-PE2702-01-01 | 13.2 | 29103-ET-PE2702-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2702-1-R-2 | 29103-ET-PE2702-1 | 29103-HTP-005 HTC-01 | PRODUCED EMULSION | 29103-65R-ET-PE2702-01-01 | 13.2 | 29103-ET-PE2702-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2802-1-R-1 | 29103-ET-PE2802-1 | 29103-HTP-005 HTC-02 | PRODUCED EMULSION | 29103-65R-ET-PE2802-01-01 | 13.2 | 29103-ET-PE2802-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2802-2-R-1 | 29103-ET-PE2802-2 | 29103-HTP-005 HTC-18 | PRODUCED EMULSION | 29103-65R-ET-PE2802-02-01 | 13.2 | 29103-ET-PE2802-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2803-1-R-1 | 29103-ET-PE2803-1 | 29103-HTP-005 HTC-21 | PRODUCED EMULSION | 29103-65R-ET-PE2803-01-01 | 13.2 | 29103-ET-PE2803-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE2803-1-R-2 | 29103-ET-PE2803-1 | 29103-HTP-005 I/O-4-1 | PRODUCED EMULSION | 29103-65R-ET-PE2803-01-01 | 13.2 | 29103-ET-PE2803-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2401-1-R-1 | 29103-ET-PG2401-1 | 29103-HTP-005 HTC-14 | PRODUCED GAS | 29103-65R-ET-PG2401-01-01 | 13.2 | 29103-ET-PG2401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2401-1-R-2 | 29103-ET-PG2401-1 | 29103-HTP-005 I/O-3-1 | PRODUCED GAS | 29103-65R-ET-PG2401-01-01 | 13.2 | 29103-ET-PG2401-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2501-1-R-1 | 29103-ET-PG2501-1 | 29103-HTP-005 HTC-11 | PRODUCED GAS | 29103-65R-ET-PG2501-01-01 | 13.2 | 29103-ET-PG2501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2501-1-R-2 | 29103-ET-PG2501-1 | 29103-HTP-005 I/O-3-2 | PRODUCED GAS | 29103-65R-ET-PG2501-01-01 | 13.2 | 29103-ET-PG2501-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2501-2-R-1 | 29103-ET-PG2501-2 | 29103-HTP-005 HTC-13 | PRODUCED GAS | 29103-65R-ET-PG2501-02-01 | 13.2 | 29103-ET-PG2501-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2601-1-R-1 | 29103-ET-PG2601-1 | 29103-HTP-005 HTC-28 | PRODUCED GAS | 29103-65R-ET-PG2601-01-01 | 13.2 | 29103-ET-PG2601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2601-1-R-2 | 29103-ET-PG2601-1 | 29103-HTP-005 HTC-15 | PRODUCED GAS | 29103-65R-ET-PG2601-01-01 | 13.2 | 29103-ET-PG2601-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2601-2-R-1 | 29103-ET-PG2601-2 | 29103-HTP-005 HTC-19 | PRODUCED GAS | 29103-65R-ET-PG2601-02-01 | 13.2 | 29103-ET-PG2601-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2701-1-R-1 | 29103-ET-PG2701-1 | 29103-HTP-005 HTC-23 | PRODUCED GAS | 29103-65R-ET-PG2701-01-01 | 13.2 | 29103-ET-PG2701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2701-1-R-2 | 29103-ET-PG2701-1 | 29103-HTP-005 HTC-16 | PRODUCED GAS | 29103-65R-ET-PG2701-01-01 | 13.2 | 29103-ET-PG2701-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG2701-2-R-1 | 29103-ET-PG2701-2 | 29103-HTP-005 HTC-30 | PRODUCED GAS | 29103-65R-ET-PG2701-02-01 | 13.2 | 29103-ET-PG2701-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD Cable | 29103-ET-P2401-1-R-1 | 29103-ET-P2401-1 | 29103-HTP-005 HTC-05 | 29103-HTP-005 |  | 113 | 29103-ET-P2401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2501-1-R-1 | 29103-ET-P2501-1 | 29103-HTP-005 HTC-04 | 29103-HTP-005 |  | 113 | 29103-ET-P2501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2504-1-R-1 | 29103-ET-P2504-1 | 29103-HTP-005 HTC-09 | 29103-HTP-005 |  | 113 | 29103-ET-P2504-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2504-1-R-2 | 29103-ET-P2504-1 | 29103-HTP-005 I/O-1-4 | 29103-HTP-005 |  | 113 | 29103-ET-P2504-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2504-2-R-1 | 29103-ET-P2504-2 | 29103-HTP-005 HTC-20 | 29103-HTP-005 |  | 113 | 29103-ET-P2504-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2504-2-R-2 | 29103-ET-P2504-2 | 29103-HTP-005 I/O-3-4 | 29103-HTP-005 |  | 113 | 29103-ET-P2504-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2601-1-R-1 | 29103-ET-P2601-1 | 29103-HTP-005 HTC-35 | 29103-HTP-005 |  | 113 | 29103-ET-P2601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2604-1-R-1 | 29103-ET-P2604-1 | 29103-HTP-005 HTC-32 | 29103-HTP-005 |  | 113 | 29103-ET-P2604-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2604-1-R-2 | 29103-ET-P2604-1 | 29103-HTP-005 I/O-2-1 | 29103-HTP-005 |  | 113 | 29103-ET-P2604-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2604-2-R-1 | 29103-ET-P2604-2 | 29103-HTP-005 HTC-24 | 29103-HTP-005 |  | 113 | 29103-ET-P2604-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2604-2-R-2 | 29103-ET-P2604-2 | 29103-HTP-005 I/O-2-2 | 29103-HTP-005 |  | 113 | 29103-ET-P2604-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2701-1-R-1 | 29103-ET-P2701-1 | 29103-HTP-005 HTC-22 | 29103-HTP-005 |  | 113 | 29103-ET-P2701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2704-1-R-1 | 29103-ET-P2704-1 | 29103-HTP-005 HTC-29 | 29103-HTP-005 |  | 113 | 29103-ET-P2704-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2704-1-R-2 | 29103-ET-P2704-1 | 29103-HTP-005 I/O-4-2 | 29103-HTP-005 |  | 113 | 29103-ET-P2704-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2704-2-R-1 | 29103-ET-P2704-2 | 29103-HTP-005 HTC-27 | 29103-HTP-005 |  | 113 | 29103-ET-P2704-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2704-2-R-2 | 29103-ET-P2704-2 | 29103-HTP-005 I/O-4-3 | 29103-HTP-005 |  | 113 | 29103-ET-P2704-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P2800-1-R-1 | 29103-ET-P2800-1 | 29103-HTP-005 HTC-17 | 29103-HTP-005 |  | 113 | 29103-ET-P2800-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2401-1-R-1 | 29103-ET-PE2401-1 | 29103-HTP-005 HTC-08 | 29103-HTP-005 |  | 113 | 29103-ET-PE2401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2501-1-R-1 | 29103-ET-PE2501-1 | 29103-HTP-005 HTC-10 | 29103-HTP-005 |  | 113 | 29103-ET-PE2501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2501-2-R-2 | 29103-ET-PE2501-2 | 29103-HTP-005 I/O-2-3 | 29103-HTP-005 |  | 113 | 29103-ET-PE2501-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2502-1-R-1 | 29103-ET-PE2502-1 | 29103-HTP-005 HTC-06 | 29103-HTP-005 |  | 113 | 29103-ET-PE2502-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2502-1-R-2 | 29103-ET-PE2502-1 | 29103-HTP-005 I/O-2-4 | 29103-HTP-005 |  | 113 | 29103-ET-PE2502-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2601-1-R-1 | 29103-ET-PE2601-1 | 29103-HTP-005 HTC-31 | 29103-HTP-005 |  | 113 | 29103-ET-PE2601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2601-2-R-2 | 29103-ET-PE2601-2 | 29103-HTP-005 I/O-1-3 | 29103-HTP-005 |  | 113 | 29103-ET-PE2601-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2602-1-R-1 | 29103-ET-PE2602-1 | 29103-HTP-005 HTC-25 | 29103-HTP-005 |  | 113 | 29103-ET-PE2602-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2602-1-R-2 | 29103-ET-PE2602-1 | 29103-HTP-005 I/O-3-3 | 29103-HTP-005 |  | 113 | 29103-ET-PE2602-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2701-1-R-1 | 29103-ET-PE2701-1 | 29103-HTP-005 HTC-33 | 29103-HTP-005 |  | 113 | 29103-ET-PE2701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2701-2-R-2 | 29103-ET-PE2701-2 | 29103-HTP-005 I/O-4-4 | 29103-HTP-005 |  | 113 | 29103-ET-PE2701-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2702-1-R-1 | 29103-ET-PE2702-1 | 29103-HTP-005 HTC-26 | 29103-HTP-005 |  | 113 | 29103-ET-PE2702-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2702-1-R-2 | 29103-ET-PE2702-1 | 29103-HTP-005 HTC-01 | 29103-HTP-005 |  | 113 | 29103-ET-PE2702-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2802-1-R-1 | 29103-ET-PE2802-1 | 29103-HTP-005 HTC-02 | 29103-HTP-005 |  | 113 | 29103-ET-PE2802-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2802-2-R-1 | 29103-ET-PE2802-2 | 29103-HTP-005 HTC-18 | 29103-HTP-005 |  | 113 | 29103-ET-PE2802-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2803-1-R-1 | 29103-ET-PE2803-1 | 29103-HTP-005 HTC-21 | 29103-HTP-005 |  | 113 | 29103-ET-PE2803-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE2803-1-R-2 | 29103-ET-PE2803-1 | 29103-HTP-005 I/O-4-1 | 29103-HTP-005 |  | 113 | 29103-ET-PE2803-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2401-1-R-1 | 29103-ET-PG2401-1 | 29103-HTP-005 HTC-14 | 29103-HTP-005 |  | 113 | 29103-ET-PG2401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2401-1-R-2 | 29103-ET-PG2401-1 | 29103-HTP-005 I/O-3-1 | 29103-HTP-005 |  | 113 | 29103-ET-PG2401-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2501-1-R-1 | 29103-ET-PG2501-1 | 29103-HTP-005 HTC-11 | 29103-HTP-005 |  | 113 | 29103-ET-PG2501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2501-1-R-2 | 29103-ET-PG2501-1 | 29103-HTP-005 I/O-3-2 | 29103-HTP-005 |  | 113 | 29103-ET-PG2501-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2501-2-R-1 | 29103-ET-PG2501-2 | 29103-HTP-005 HTC-13 | 29103-HTP-005 |  | 113 | 29103-ET-PG2501-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2601-1-R-1 | 29103-ET-PG2601-1 | 29103-HTP-005 HTC-28 | 29103-HTP-005 |  | 113 | 29103-ET-PG2601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2601-1-R-2 | 29103-ET-PG2601-1 | 29103-HTP-005 HTC-15 | 29103-HTP-005 |  | 113 | 29103-ET-PG2601-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2601-2-R-1 | 29103-ET-PG2601-2 | 29103-HTP-005 HTC-19 | 29103-HTP-005 |  | 113 | 29103-ET-PG2601-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2701-1-R-1 | 29103-ET-PG2701-1 | 29103-HTP-005 HTC-23 | 29103-HTP-005 |  | 113 | 29103-ET-PG2701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2701-1-R-2 | 29103-ET-PG2701-1 | 29103-HTP-005 HTC-16 | 29103-HTP-005 |  | 113 | 29103-ET-PG2701-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG2701-2-R-1 | 29103-ET-PG2701-2 | 29103-HTP-005 HTC-30 | 29103-HTP-005 |  | 113 | 29103-ET-PG2701-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-012 |  | 29103-HTP-005 HTC-07 | 29103-HTP-005 |  | 113 | 29103-RJB-012.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-013 |  | 29103-HTP-005 HTC-12 | 29103-HTP-005 |  | 113 | 29103-RJB-013.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-014 |  | 29103-HTP-005 HTC-03 | 29103-HTP-005 |  | 113 | 29103-RJB-014.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup

## 29103-HTP-003
29103-HTP-003
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29103-ET-FG1305-1-1 | 29103-ET-FG1305-1 | 29103-AMB-004 | 29103-FG-1306, 29103-FG-1305 | 29103-65R-ET-FG1305-01-01 | 13.1 | 29103-ET-FG1305-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 343.5 Ω | 2026-05-17 | [12 empty] | D/32SA2600/16.9M/230/277/1.2M/LS23A/X/N12 | 16.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1501-1-1 | 29103-ET-FG1501-1 | 29103-AMB-005 | 29103-FG-1501 | 29103-65R-ET-FG1501-01-01 | 13.1 | 29103-ET-FG1501-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 23.4 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1501-1-2 | 29103-ET-FG1501-1 | 29103-AMB-005 |  | 29103-65R-ET-FG1501-01-01 | 13.1 | 29103-ET-FG1501-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 1.2 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1503-1-1 | 29103-ET-FG1503-1 | 29103-AMB-005 | 29103-FG-1503 | 29103-65R-ET-FG1503-01-01 | 13.1 | 29103-ET-FG1503-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 12.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1503-1-2 | 29103-ET-FG1503-1 | 29103-AMB-005 | 29103-FG-1503 | 29103-65R-ET-FG1503-01-01 | 13.1 | 29103-ET-FG1503-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 14.4 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1503-1-3 | 29103-ET-FG1503-1 | 29103-AMB-005 |  | 29103-65R-ET-FG1503-01-01 | 13.1 | 29103-ET-FG1503-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1503-1-4 | 29103-ET-FG1503-1 | 29103-AMB-005 |  | 29103-65R-ET-FG1503-01-01 | 13.1 | 29103-ET-FG1503-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1505-1-1 | 29103-ET-FG1505-1 | 29103-AMB-006 | 29103-FG-1506, 29103-FG-1505 | 29103-65R-ET-FG1505-01-01 | 13.1 | 29103-ET-FG1505-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 341.3 Ω | 2026-05-17 | [12 empty] | D/32SA2600/16.9M/230/277/1.2M/LS23A/X/N12 | 16.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1601-1-1 | 29103-ET-FG1601-1 | 29103-AMB-005 | 29103-FG-1601 | 29103-65R-ET-FG1601-01-01 | 13.1 | 29103-ET-FG1601-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 24.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1603-1-1 | 29103-ET-FG1603-1 | 29103-AMB-005 | 29103-FG-1603 | 29103-65R-ET-FG1603-01-01 | 13.1 | 29103-ET-FG1603-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 12.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1603-1-2 | 29103-ET-FG1603-1 | 29103-AMB-005 | 29103-FG-1603 | 29103-65R-ET-FG1603-01-01 | 13.1 | 29103-ET-FG1603-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1603-1-3 | 29103-ET-FG1603-1 | 29103-AMB-005 |  | 29103-65R-ET-FG1603-01-01 | 13.1 | 29103-ET-FG1603-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1603-1-4 | 29103-ET-FG1603-1 | 29103-AMB-005 |  | 29103-65R-ET-FG1603-01-01 | 13.1 | 29103-ET-FG1603-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1701-1-1 | 29103-ET-FG1701-1 | HTC-39 / CB-39 | 29103-FG-1701 | 29103-65R-ET-FG1701-01-01 | 13.1 | 29103-ET-FG1701-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 23.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1703-1-1 | 29103-ET-FG1703-1 | HTC-40 / CB-40 | 29103-FG-1703 | 29103-65R-ET-FG1703-01-01 | 13.1 | 29103-ET-FG1703-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1703-1-2 | 29103-ET-FG1703-1 | HTC-40 / CB-40 | 29103-FG-1703 | 29103-65R-ET-FG1703-01-01 | 13.1 | 29103-ET-FG1703-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 11.7 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1703-1-3 | 29103-ET-FG1703-1 | HTC-40 / CB-40 |  | 29103-65R-ET-FG1703-01-01 | 13.1 | 29103-ET-FG1703-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1703-1-4 | 29103-ET-FG1703-1 | HTC-40 / CB-40 |  | 29103-65R-ET-FG1703-01-01 | 13.1 | 29103-ET-FG1703-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1404-1-1 | 29103-ET-P1404-1 | HTC-34 / CB-34 | 29103-PE-1401, 29103-P-1404 | 29103-65R-ET-P1404-01-01 | 13.1 | 29103-ET-P1404-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1404-1-2 | 29103-ET-P1404-1 | HTC-34 / CB-34 | 29103-P-1404 | 29103-65R-ET-P1404-01-01 | 13.1 | 29103-ET-P1404-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 10.6 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/6.5M/416/67.7/1.2M/LS23A/X/N12/XNF | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P1404-1-3 | 29103-ET-P1404-1 | HTC-34 / CB-34 | 29103-P-1404 | 29103-65R-ET-P1404-01-01 | 13.1 | 29103-ET-P1404-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/448/72.9/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1404-1-4 | 29103-ET-P1404-1 | HTC-34 / CB-34 | 29103-P-1404 | 29103-65R-ET-P1404-01-01 | 13.1 | 29103-ET-P1404-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/838/136/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1404-2-1 | 29103-ET-P1404-2 | HTC-26 / CB-26 | 29103-P-1404, 29103-FG-1402 | 29103-65R-ET-P1404-02-01 | 13.1 | 29103-ET-P1404-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 260.9 Ω | 2026-05-17 | [12 empty] | D/32SF1110/7M/299/277/1.2M/LS23A/X/N12 | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1501-1-1 | 29103-ET-P1501-1 | HTC-04 / CB-04 | 29103-P-1501 | 29103-65R-ET-P1501-01-01 | 13.1 | 29103-ET-P1501-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.5M/1007/166/1.2M/LS23A/X/N12/XNF | 20.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P1501-1-2 | 29103-ET-P1501-1 | HTC-04 / CB-04 | 29103-P-1501 | 29103-65R-ET-P1501-01-01 | 13.1 | 29103-ET-P1501-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.8M/678/111/1.2M/LS23A/X/N12/XMN | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1504-1-1 | 29103-ET-P1504-1 | HTC-02 / CB-02 | 29103-PE-1501, 29103-P-1504 | 29103-65R-ET-P1504-01-01 | 13.1 | 29103-ET-P1504-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1504-1-2 | 29103-ET-P1504-1 | HTC-02 / CB-02 | 29103-P-1504 | 29103-65R-ET-P1504-01-01 | 13.1 | 29103-ET-P1504-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.8 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/8M/461/78.9/1.2M/LS23A/X/N12/XNF | 8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1504-1-3 | 29103-ET-P1504-1 | HTC-02 / CB-02 | 29103-P-1504 | 29103-65R-ET-P1504-01-01 | 13.1 | 29103-ET-P1504-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/403/69/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1504-1-4 | 29103-ET-P1504-1 | HTC-02 / CB-02 | 29103-P-1504 | 29103-65R-ET-P1504-01-01 | 13.1 | 29103-ET-P1504-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 21 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/755/129/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1504-2-1 | 29103-ET-P1504-2 | HTC-27 / CB-27 | 29103-P-1504, 29103-P-1304, 29103-FG-1502 | 29103-65R-ET-P1504-02-01 | 13.1 | 29103-ET-P1504-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 375.9 Ω | 2026-05-17 | [12 empty] | D/32SF1180/6.2M/207/277/1.2M/LS23A/X/N12 | 6.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P1601-1-1 | 29103-ET-P1601-1 | HTC-05 / CB-05 | 29103-P-1601 | 29103-65R-ET-P1601-01-01 | 13.1 | 29103-ET-P1601-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.6M/1001/165/1.2M/LS23A/X/N12/XNF | 20.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P1601-1-2 | 29103-ET-P1601-1 | HTC-05 / CB-05 | 29103-P-1601 | 29103-65R-ET-P1601-01-01 | 13.1 | 29103-ET-P1601-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.9M/676/112/1.2M/LS23A/X/N12/XMN | 13.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1604-1-1 | 29103-ET-P1604-1 | HTC-09 / CB-09 | 29103-PE-1601, 29103-P-1604 | 29103-65R-ET-P1604-01-01 | 13.1 | 29103-ET-P1604-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1604-1-2 | 29103-ET-P1604-1 | HTC-09 / CB-09 | 29103-P-1604 | 29103-65R-ET-P1604-01-01 | 13.1 | 29103-ET-P1604-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 10.6 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/6.5M/416/67.7/1.2M/LS23A/X/N12/XNF | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P1604-1-3 | 29103-ET-P1604-1 | HTC-09 / CB-09 | 29103-P-1604 | 29103-65R-ET-P1604-01-01 | 13.1 | 29103-ET-P1604-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/448/72.9/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1604-1-4 | 29103-ET-P1604-1 | HTC-09 / CB-09 | 29103-P-1604 | 29103-65R-ET-P1604-01-01 | 13.1 | 29103-ET-P1604-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/838/136/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1604-2-1 | 29103-ET-P1604-2 | HTC-17 / CB-17 | 29103-P-1604, 29103-FG-1602 | 29103-65R-ET-P1604-02-01 | 13.1 | 29103-ET-P1604-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 262.6 Ω | 2026-05-17 | [12 empty] | D/32SF1110/7M/299/277/1.2M/LS23A/X/N12 | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1701-1-1 | 29103-ET-P1701-1 | HTC-19 / CB-19 | 29103-P-1701 | 29103-65R-ET-P1701-01-01 | 13.1 | 29103-ET-P1701-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.5M/1007/166/1.2M/LS23A/X/N12/XNF | 20.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P1701-1-2 | 29103-ET-P1701-1 | HTC-19 / CB-19 | 29103-P-1701 | 29103-65R-ET-P1701-01-01 | 13.1 | 29103-ET-P1701-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.8M/678/111/1.2M/LS23A/X/N12/XMN | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1704-1-1 | 29103-ET-P1704-1 | HTC-18 / CB-18 | 29103-PE-1701, 29103-P-1704 | 29103-65R-ET-P1704-01-01 | 13.1 | 29103-ET-P1704-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1704-1-2 | 29103-ET-P1704-1 | HTC-18 / CB-18 | 29103-P-1704 | 29103-65R-ET-P1704-01-01 | 13.1 | 29103-ET-P1704-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.9 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/8M/461/78.9/1.2M/LS23A/X/N12/XNF | 8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1704-1-3 | 29103-ET-P1704-1 | HTC-18 / CB-18 | 29103-P-1704 | 29103-65R-ET-P1704-01-01 | 13.1 | 29103-ET-P1704-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/403/69/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1704-1-4 | 29103-ET-P1704-1 | HTC-18 / CB-18 | 29103-P-1704 | 29103-65R-ET-P1704-01-01 | 13.1 | 29103-ET-P1704-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 21 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/755/129/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1704-2-1 | 29103-ET-P1704-2 | HTC-32 / CB-32 | 29103-P-1704, 29103-P-1304, 29103-FG-1702 | 29103-65R-ET-P1704-02-01 | 13.1 | 29103-ET-P1704-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 372.7 Ω | 2026-05-17 | [12 empty] | D/32SF1180/6.2M/207/277/1.2M/LS23A/X/N12 | 6.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-3-1 | 29103-ET-P1800-3 | HTC-24 / CB-24 | 29103-P-1800 | 29103-65R-ET-P1800-03-01 | 13.1 | 29103-ET-P1800-3-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/9.7M/555/84.8/2.1M/LS23A/X/N12/XNF | 9.7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-3-2 | 29103-ET-P1800-3 | HTC-24 / CB-24 | 29103-P-1800 | 29103-65R-ET-P1800-03-01 | 13.1 | 29103-ET-P1800-3-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/9.7M/555/84.8/2.1M/LS23A/X/N12/XNF | 9.7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-3-3 | 29103-ET-P1800-3 | HTC-24 / CB-24 | 29103-P-1800 | 29103-65R-ET-P1800-03-01 | 13.1 | 29103-ET-P1800-3-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/22M/1258/192/2.1M/LS23A/X/N12/XMN | 22 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-3-4 | 29103-ET-P1800-3 | HTC-24 / CB-24 | 29103-P-1800 | 29103-65R-ET-P1800-03-01 | 13.1 | 29103-ET-P1800-3-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/22M/1258/192/2.1M/LS23A/X/N12/XMN | 22 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1401-2-1 | 29103-ET-PE1401-2 | HTC-30 / CB-30 | 29103-PE-1401 | 29103-65R-ET-PE1401-02-01 | 13.1 | 29103-ET-PE1401-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.1M/2079/277/1.2M/LS23A/X/N12 | 52.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1401-2-2 | 29103-ET-PE1401-2 | HTC-30 / CB-30 | 29103-PE-1401 | 29103-65R-ET-PE1401-02-01 | 13.1 | 29103-ET-PE1401-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.2M/701/277/1.2M/LS23A/X/N12 | 29.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1402-1-1 | 29103-ET-PE1402-1 | HTC-33 / CB-33 | 29103-PE-1403, 29103-PE-1402 | 29103-65R-ET-PE1402-01-01 | 13.1 | 29103-ET-PE1402-1-1.pdf | YES | YES | NO | YES | NO | N/A | N/A | N/A | N/A | YES | NO | 2 |  |  |  | 0.0 MΩ | 44.9 Ω | 2026-08-12 | [9 empty] | D/32SQ3374/35.4M/1635/277/1.2M/LS23A/X/N12 | 35.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1501-1-1 | 29103-ET-PE1501-1 | HTC-10 / CB-10 | 29103-PE-1501 | 29103-65R-ET-PE1501-01-01 | 13.1 | 29103-ET-PE1501-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.8M/269/277/1.2M/LS23A/X/N12 | 7.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1501-1-2 | 29103-ET-PE1501-1 | HTC-10 / CB-10 | 29103-PE-1501 | 29103-65R-ET-PE1501-01-01 | 13.1 | 29103-ET-PE1501-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/9.5M/505/89.8/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1501-1-3 | 29103-ET-PE1501-1 | HTC-10 / CB-10 | 29103-PE-1501 | 29103-65R-ET-PE1501-01-01 | 13.1 | 29103-ET-PE1501-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/351/62.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1501-1-4 | 29103-ET-PE1501-1 | HTC-10 / CB-10 | 29103-PE-1501 | 29103-65R-ET-PE1501-01-01 | 13.1 | 29103-ET-PE1501-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.2M/702/125/1.2M/LS23A/X/N12/XMN | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1501-2-1 | 29103-ET-PE1501-2 | HTC-07 / CB-07 | 29103-PE-1501 | 29103-65R-ET-PE1501-02-01 | 13.1 | 29103-ET-PE1501-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.5M/2063/277/1.2M/LS23A/X/N12 | 52.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1501-2-2 | 29103-ET-PE1501-2 | HTC-07 / CB-07 | 29103-PE-1501 | 29103-65R-ET-PE1501-02-01 | 13.1 | 29103-ET-PE1501-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.4M/694/277/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1502-1-1 | 29103-ET-PE1502-1 | HTC-06 / CB-06 | 29103-PE-1503, 29103-PE-1502 | 29103-65R-ET-PE1502-01-01 | 13.1 | 29103-ET-PE1502-1-1.pdf | YES | YES | NO | YES | NO | N/A | N/A | N/A | N/A | YES | NO | 3 |  |  |  | 550 MΩ | 44.7 Ω | 2026-08-10 | [9 empty] | D/32SQ3374/34.9M/1658/277/1.2M/LS23A/X/N12 | 34.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1601-1-1 | 29103-ET-PE1601-1 | HTC-08 / CB-08 | 29103-PE-1601 | 29103-65R-ET-PE1601-01-01 | 13.1 | 29103-ET-PE1601-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.5M/280/277/1.2M/LS23A/X/N12 | 7.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1601-1-2 | 29103-ET-PE1601-1 | HTC-08 / CB-08 | 29103-PE-1601 | 29103-65R-ET-PE1601-01-01 | 13.1 | 29103-ET-PE1601-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/10.8M/522/97.1/1.2M/LS23A/X/N12/XNF | 10.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1601-1-3 | 29103-ET-PE1601-1 | HTC-08 / CB-08 | 29103-PE-1601 | 29103-65R-ET-PE1601-01-01 | 13.1 | 29103-ET-PE1601-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/319/59.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1601-1-4 | 29103-ET-PE1601-1 | HTC-08 / CB-08 | 29103-PE-1601 | 29103-65R-ET-PE1601-01-01 | 13.1 | 29103-ET-PE1601-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.4M/647/121/1.2M/LS23A/X/N12/XMN | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1601-2-1 | 29103-ET-PE1601-2 | HTC-12 / CB-12 | 29103-PE-1601 | 29103-65R-ET-PE1601-02-01 | 13.1 | 29103-ET-PE1601-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.1M/2079/277/1.2M/LS23A/X/N12 | 52.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1601-2-2 | 29103-ET-PE1601-2 | HTC-12 / CB-12 | 29103-PE-1601 | 29103-65R-ET-PE1601-02-01 | 13.1 | 29103-ET-PE1601-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.2M/701/277/1.2M/LS23A/X/N12 | 29.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1602-1-1 | 29103-ET-PE1602-1 | HTC-15 / CB-15 | 29103-PE-1603, 29103-PE-1602 | 29103-65R-ET-PE1602-01-01 | 13.1 | 29103-ET-PE1602-1-1.pdf | YES | YES | NO | YES | NO | N/A | N/A | N/A | N/A | YES | NO | 4 |  |  |  | 550 MΩ | 44.7 Ω | 2026-08-10 | [9 empty] | D/32SQ3374/35.4M/1635/277/1.2M/LS23A/X/N12 | 35.4 m m | Levy Ostrup |  | Core markers are 29103HTP003HTC15-P-H and 29103HTP003HTC15-P-N
EHT Trace | 29103-ET-PE1701-1-1 | 29103-ET-PE1701-1 | HTC-23 / CB-23 | 29103-PE-1701 | 29103-65R-ET-PE1701-01-01 | 13.1 | 29103-ET-PE1701-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.8M/269/277/1.2M/LS23A/X/N12 | 7.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1701-1-2 | 29103-ET-PE1701-1 | HTC-23 / CB-23 | 29103-PE-1701 | 29103-65R-ET-PE1701-01-01 | 13.1 | 29103-ET-PE1701-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/9.5M/505/89.8/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1701-1-3 | 29103-ET-PE1701-1 | HTC-23 / CB-23 | 29103-PE-1701 | 29103-65R-ET-PE1701-01-01 | 13.1 | 29103-ET-PE1701-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/351/62.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1701-1-4 | 29103-ET-PE1701-1 | HTC-23 / CB-23 | 29103-PE-1701 | 29103-65R-ET-PE1701-01-01 | 13.1 | 29103-ET-PE1701-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.2M/702/125/1.2M/LS23A/X/N12/XMN | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1701-2-1 | 29103-ET-PE1701-2 | HTC-16 / CB-16 | 29103-PE-1701 | 29103-65R-ET-PE1701-02-01 | 13.1 | 29103-ET-PE1701-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.5M/2063/277/1.2M/LS23A/X/N12 | 52.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1701-2-2 | 29103-ET-PE1701-2 | HTC-16 / CB-16 | 29103-PE-1701 | 29103-65R-ET-PE1701-02-01 | 13.1 | 29103-ET-PE1701-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.4M/694/277/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1702-1-1 | 29103-ET-PE1702-1 | HTC-20 / CB-20 | 29103-PE-1703, 29103-PE-1702 | 29103-65R-ET-PE1702-01-01 | 13.1 | 29103-ET-PE1702-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/34.9M/1658/277/1.2M/LS23A/X/N12 | 34.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-2-1 | 29103-ET-PE1802-2 | HTC-13 / CB-13 | 29103-PE-1802 | 29103-65R-ET-PE1802-02-01 | 13.1 | 29103-ET-PE1802-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3150/8.8M/784/61.6/2.1-1.2M/LS23A/X/N12/XNF | 8.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-2-2 | 29103-ET-PE1802-2 | HTC-13 / CB-13 | 29103-PE-1802 | 29103-65R-ET-PE1802-02-01 | 13.1 | 29103-ET-PE1802-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3150/21.6M/1925/151/1.2M/LS23A/X/N12/XMF | 21.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-2-3 | 29103-ET-PE1802-2 | HTC-13 / CB-13 | 29103-PE-1802 | 29103-65R-ET-PE1802-02-01 | 13.1 | 29103-ET-PE1802-2-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3150/9.2M/820/64.4/1.2M/LS23A/X/N12/XMN | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-2-1 | 29103-ET-PE1803-2 | HTC-29 / CB-29 | 29103-PE-1803 | 29103-65R-ET-PE1803-02-01 | 13.1 | 29103-ET-PE1803-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/11.3M/542/90.2/1.2M/LS23A/X/N12/XNF | 11.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-2-2 | 29103-ET-PE1803-2 | HTC-29 / CB-29 | 29103-PE-1803 | 29103-65R-ET-PE1803-02-01 | 13.1 | 29103-ET-PE1803-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/23.4M/1123/187/1.2M/LS23A/X/N12/XMN | 23.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1401-1-1 | 29103-ET-PG1401-1 | HTC-35 / CB-35 | 29103-PG-1401, 29103-PE-1402, 29103-P-1400 | 29103-65R-ET-PG1401-01-01 | 13.1 | 29103-ET-PG1401-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/93.1M/2914/277/1.2M/LS23A/X/N12 | 93.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1401-2-1 | 29103-ET-PG1401-2 | HTC-22 / CB-22 | 29103-PG-1401 | 29103-65R-ET-PG1401-02-01 | 13.1 | 29103-ET-PG1401-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/8.6M/401/89.2/1.2M/LS23A/X/N12/XNF | 8.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1401-2-2 | 29103-ET-PG1401-2 | HTC-22 / CB-22 | 29103-PG-1401 | 29103-65R-ET-PG1401-02-01 | 13.1 | 29103-ET-PG1401-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/6.3M/294/65.4/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1401-2-3 | 29103-ET-PG1401-2 | HTC-22 / CB-22 | 29103-PG-1401 | 29103-65R-ET-PG1401-02-01 | 13.1 | 29103-ET-PG1401-2-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/11.8M/550/122/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1501-1-1 | 29103-ET-PG1501-1 | HTC-11 / CB-11 | 29103-PG-1501, 29103-PE-1502, 29103-P-1500 | 29103-65R-ET-PG1501-01-01 | 13.1 | 29103-ET-PG1501-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/90M/3006/277/1.2M/LS23A/X/N12 | 90 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1501-2-1 | 29103-ET-PG1501-2 | HTC-28 / CB-28 | 29103-PG-1501 | 29103-65R-ET-PG1501-02-01 | 13.1 | 29103-ET-PG1501-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/9.2M/409/93.3/1.2M/LS23A/X/N12/XNF | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1501-2-2 | 29103-ET-PG1501-2 | HTC-28 / CB-28 | 29103-PG-1501 | 29103-65R-ET-PG1501-02-01 | 13.1 | 29103-ET-PG1501-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/6.3M/280/63.9/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1501-2-3 | 29103-ET-PG1501-2 | HTC-28 / CB-28 | 29103-PG-1501 | 29103-65R-ET-PG1501-02-01 | 13.1 | 29103-ET-PG1501-2-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/11.8M/525/120/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1601-1-1 | 29103-ET-PG1601-1 | HTC-14 / CB-14 | 29103-PG-1601, 29103-PE-1602, 29103-P-1600 | 29103-65R-ET-PG1601-01-01 | 13.1 | 29103-ET-PG1601-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/93.1M/2914/277/1.2M/LS23A/X/N12 | 93.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1601-2-1 | 29103-ET-PG1601-2 | HTC-31 / CB-31 | 29103-PG-1601 | 29103-65R-ET-PG1601-02-01 | 13.1 | 29103-ET-PG1601-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/8.6M/401/89.2/1.2M/LS23A/X/N12/XNF | 8.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1601-2-2 | 29103-ET-PG1601-2 | HTC-31 / CB-31 | 29103-PG-1601 | 29103-65R-ET-PG1601-02-01 | 13.1 | 29103-ET-PG1601-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 14.9 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/294/65.4/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1601-2-3 | 29103-ET-PG1601-2 | HTC-31 / CB-31 | 29103-PG-1601 | 29103-65R-ET-PG1601-02-01 | 13.1 | 29103-ET-PG1601-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/550/122/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1701-1-1 | 29103-ET-PG1701-1 | HTC-21 / CB-21 | 29103-PG-1701, 29103-PE-1702, 29103-P-1700 | 29103-65R-ET-PG1701-01-01 | 13.1 | 29103-ET-PG1701-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/90M/3006/277/1.2M/LS23A/X/N12 | 90 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1701-2-1 | 29103-ET-PG1701-2 | HTC-25 / CB-25 | 29103-PG-1701 | 29103-65R-ET-PG1701-02-01 | 13.1 | 29103-ET-PG1701-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 21.8 Ω | 2026-05-18 | [12 empty] | E/32SB3700/9.2M/409/93.3/1.2M/LS23A/X/N12/XNF | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1701-2-2 | 29103-ET-PG1701-2 | HTC-25 / CB-25 | 29103-PG-1701 | 29103-65R-ET-PG1701-02-01 | 13.1 | 29103-ET-PG1701-2-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 15 Ω | 2026-05-18 | [12 empty] | E/32SB3700/6.3M/280/63.9/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1701-2-3 | 29103-ET-PG1701-2 | HTC-25 / CB-25 | 29103-PG-1701 | 29103-65R-ET-PG1701-02-01 | 13.1 | 29103-ET-PG1701-2-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 28.2 Ω | 2026-05-18 | [12 empty] | D/32SB3700/11.8M/525/120/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1303-1-1 | 29103-ET-ST1303-1 | 29103-AMB-004 | 29103-ST-1304, 29103-ST-1303 | 29103-65R-ET-ST1303-01-01 | 13.1 | 29103-ET-ST1303-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.5M/282/136/1.2M/LS23A/X/N12/XNF | 17.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1303-1-2 | 29103-ET-ST1303-1 | 29103-AMB-004 | 29103-ST-1304 | 29103-65R-ET-ST1303-01-01 | 13.1 | 29103-ET-ST1303-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/293/141/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1303-1-3 | 29103-ET-ST1303-1 | 29103-AMB-004 | 29103-ST-1303 | 29103-65R-ET-ST1303-01-01 | 13.1 | 29103-ET-ST1303-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 55.4 Ω | 2026-05-18 | [12 empty] | E/32SA2170/9.5M/162/93/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1303-1-4 | 29103-ET-ST1303-1 | 29103-AMB-004 | 29103-ST-1303 | 29103-65R-ET-ST1303-01-01 | 13.1 | 29103-ET-ST1303-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 33.8 Ω | 2026-05-18 | [12 empty] | E/32SA2170/5.7M/97/55.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1303-1-5 | 29103-ET-ST1303-1 | 29103-AMB-004 | 29103-ST-1303 | 29103-65R-ET-ST1303-01-01 | 13.1 | 29103-ET-ST1303-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 76.2 Ω | 2026-05-18 | [12 empty] | D/32SA2170/13.1M/224/128/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1403-1-1 | 29103-ET-ST1403-1 | 29103-AMB-004 | 29103-ST-1404, 29103-ST-1403 | 29103-65R-ET-ST1403-01-01 | 13.1 | 29103-ET-ST1403-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.3M/282/135/1.2M/LS23A/X/N12/XNF | 17.3 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1403-1-2 | 29103-ET-ST1403-1 | 29103-AMB-004 | 29103-ST-1404 | 29103-65R-ET-ST1403-01-01 | 13.1 | 29103-ET-ST1403-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/297/142/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1403-1-3 | 29103-ET-ST1403-1 | 29103-AMB-004 | 29103-ST-1403 | 29103-65R-ET-ST1403-01-01 | 13.1 | 29103-ET-ST1403-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 51.8 Ω | 2026-05-18 | [12 empty] | E/32SA2200/7.6M/127/79.7/1.2M/LS23A/X/N12/XNF | 7.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1403-1-4 | 29103-ET-ST1403-1 | 29103-AMB-004 | 29103-ST-1403 | 29103-65R-ET-ST1403-01-01 | 13.1 | 29103-ET-ST1403-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 38.7 Ω | 2026-05-18 | [12 empty] | E/32SA2200/5.7M/95/59.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1403-1-5 | 29103-ET-ST1403-1 | 29103-AMB-004 | 29103-ST-1403 | 29103-65R-ET-ST1403-01-01 | 13.1 | 29103-ET-ST1403-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 88.3 Ω | 2026-05-18 | [12 empty] | D/32SA2200/13.1M/219/137/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1503-1-1 | 29103-ET-ST1503-1 | 29103-AMB-006 | 29103-ST-1504, 29103-ST-1503 | 29103-65R-ET-ST1503-01-01 | 13.1 | 29103-ET-ST1503-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.5M/282/136/1.2M/LS23A/X/N12/XNF | 17.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1503-1-2 | 29103-ET-ST1503-1 | 29103-AMB-006 | 29103-ST-1504 | 29103-65R-ET-ST1503-01-01 | 13.1 | 29103-ET-ST1503-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/293/141/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1503-1-3 | 29103-ET-ST1503-1 | 29103-AMB-006 | 29103-ST-1503 | 29103-65R-ET-ST1503-01-01 | 13.1 | 29103-ET-ST1503-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 55.5 Ω | 2026-05-18 | [12 empty] | E/32SA2170/9.5M/162/93/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1503-1-4 | 29103-ET-ST1503-1 | 29103-AMB-006 | 29103-ST-1503 | 29103-65R-ET-ST1503-01-01 | 13.1 | 29103-ET-ST1503-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 33.5 Ω | 2026-05-18 | [12 empty] | E/32SA2170/5.7M/97/55.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1503-1-5 | 29103-ET-ST1503-1 | 29103-AMB-006 | 29103-ST-1503 | 29103-65R-ET-ST1503-01-01 | 13.1 | 29103-ET-ST1503-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 76.1 Ω | 2026-05-18 | [12 empty] | D/32SA2170/13.1M/224/128/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1603-1-1 | 29103-ET-ST1603-1 | 29103-AMB-006 | 29103-ST-1604, 29103-ST-1603 | 29103-65R-ET-ST1603-01-01 | 13.1 | 29103-ET-ST1603-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.3M/282/135/1.2M/LS23A/X/N12/XNF | 17.3 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1603-1-2 | 29103-ET-ST1603-1 | 29103-AMB-006 | 29103-ST-1604 | 29103-65R-ET-ST1603-01-01 | 13.1 | 29103-ET-ST1603-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/297/142/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1603-1-3 | 29103-ET-ST1603-1 | 29103-AMB-006 | 29103-ST-1603 | 29103-65R-ET-ST1603-01-01 | 13.1 | 29103-ET-ST1603-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SA2200/7.6M/127/79.7/1.2M/LS23A/X/N12/XNF | 7.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1603-1-4 | 29103-ET-ST1603-1 | 29103-AMB-006 | 29103-ST-1603 | 29103-65R-ET-ST1603-01-01 | 13.1 | 29103-ET-ST1603-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SA2200/5.7M/95/59.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1603-1-5 | 29103-ET-ST1603-1 | 29103-AMB-006 | 29103-ST-1603 | 29103-65R-ET-ST1603-01-01 | 13.1 | 29103-ET-ST1603-1-5.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/13.1M/219/137/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1703-1-1 | 29103-ET-ST1703-1 | 29103-AMB-006 | 29103-ST-1704, 29103-ST-1703 | 29103-65R-ET-ST1703-01-01 | 13.1 | 29103-ET-ST1703-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.5M/282/136/1.2M/LS23A/X/N12/XNF | 17.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1703-1-2 | 29103-ET-ST1703-1 | 29103-AMB-006 | 29103-ST-1704 | 29103-65R-ET-ST1703-01-01 | 13.1 | 29103-ET-ST1703-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/293/141/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1703-1-3 | 29103-ET-ST1703-1 | 29103-AMB-006 | 29103-ST-1703 | 29103-65R-ET-ST1703-01-01 | 13.1 | 29103-ET-ST1703-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SA2170/9.5M/162/93/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1703-1-4 | 29103-ET-ST1703-1 | 29103-AMB-006 | 29103-ST-1703 | 29103-65R-ET-ST1703-01-01 | 13.1 | 29103-ET-ST1703-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SA2170/5.7M/97/55.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1703-1-5 | 29103-ET-ST1703-1 | 29103-AMB-006 | 29103-ST-1703 | 29103-65R-ET-ST1703-01-01 | 13.1 | 29103-ET-ST1703-1-5.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2170/13.1M/224/128/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
Power Cable | 29103-AMB-004 |  | 29103-HTP-003 HTC-37 | 29103-HTP-003 |  | 113 | 29103-AMB-004.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-005 |  | 29103-HTP-003 HTC-01 | 29103-HTP-003 |  | 113 | 29103-AMB-005.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-006 |  | 29103-HTP-003 HTC-03 | 29103-HTP-003 |  | 113 | 29103-AMB-006.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-FG1305-1-PWK-1 | 29103-ET-FG1305-1 | 29103-AMB-004 | 29103-HTP-003 |  | 113 | 29103-ET-FG1305-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1501-1-PWK-1 | 29103-ET-FG1501-1 | 29103-AMB-005 | 29103-HTP-003 |  | 113 | 29103-ET-FG1501-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1503-1-PWK-1 | 29103-ET-FG1503-1 | 29103-AMB-005 | 29103-HTP-003 |  | 113 | 29103-ET-FG1503-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1505-1-PWK-1 | 29103-ET-FG1505-1 | 29103-AMB-006 | 29103-HTP-003 |  | 113 | 29103-ET-FG1505-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1601-1-PWK-1 | 29103-ET-FG1601-1 | 29103-AMB-005 | 29103-HTP-003 |  | 113 | 29103-ET-FG1601-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1603-1-PWK-1 | 29103-ET-FG1603-1 | 29103-AMB-005 | 29103-HTP-003 |  | 113 | 29103-ET-FG1603-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1701-1-PWK-1 | 29103-ET-FG1701-1 | 29103-HTP-003 HTC-39 | 29103-HTP-003 |  | 113 | 29103-ET-FG1701-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1703-1-PWK-1 | 29103-ET-FG1703-1 | 29103-HTP-003 HTC-40 | 29103-HTP-003 |  | 113 | 29103-ET-FG1703-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1404-1-PWK-1 | 29103-ET-P1404-1 | 29103-HTP-003 HTC-34 | 29103-HTP-003 |  | 113 | 29103-ET-P1404-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1404-2-PWK-1 | 29103-ET-P1404-2 | 29103-HTP-003 HTC-26 | 29103-HTP-003 |  | 113 | 29103-ET-P1404-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1501-1-PWK-1 | 29103-ET-P1501-1 | 29103-HTP-003 HTC-04 | 29103-HTP-003 |  | 113 | 29103-ET-P1501-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1504-1-PWK-1 | 29103-ET-P1504-1 | 29103-HTP-003 HTC-02 | 29103-HTP-003 |  | 113 | 29103-ET-P1504-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1504-2-PWK-1 | 29103-ET-P1504-2 | 29103-HTP-003 HTC-27 | 29103-HTP-003 |  | 113 | 29103-ET-P1504-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1601-1-PWK-1 | 29103-ET-P1601-1 | 29103-HTP-003 HTC-05 | 29103-HTP-003 |  | 113 | 29103-ET-P1601-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1604-1-PWK-1 | 29103-ET-P1604-1 | 29103-HTP-003 HTC-09 | 29103-HTP-003 |  | 113 | 29103-ET-P1604-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1604-2-PWK-1 | 29103-ET-P1604-2 | 29103-HTP-003 HTC-17 | 29103-HTP-003 |  | 113 | 29103-ET-P1604-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1701-1-PWK-1 | 29103-ET-P1701-1 | 29103-HTP-003 HTC-19 | 29103-HTP-003 |  | 113 | 29103-ET-P1701-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1704-1-PWK-1 | 29103-ET-P1704-1 | 29103-HTP-003 HTC-18 | 29103-HTP-003 |  | 113 | 29103-ET-P1704-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1704-2-PWK-1 | 29103-ET-P1704-2 | 29103-HTP-003 HTC-32 | 29103-HTP-003 |  | 113 | 29103-ET-P1704-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1800-3-PWK-1 | 29103-ET-P1800-3 | 29103-HTP-003 HTC-24 | 29103-HTP-003 |  | 113 | 29103-ET-P1800-3-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1401-2-PWK-1 | 29103-ET-PE1401-2 | 29103-HTP-003 HTC-30 | 29103-HTP-003 |  | 113 | 29103-ET-PE1401-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1402-1-PWK-1 | 29103-ET-PE1402-1 | 29103-HTP-003 HTC-33 | 29103-HTP-003 |  | 113 | 29103-ET-PE1402-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1501-1-PWK-1 | 29103-ET-PE1501-1 | 29103-HTP-003 HTC-10 | 29103-HTP-003 |  | 113 | 29103-ET-PE1501-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1501-2-PWK-1 | 29103-ET-PE1501-2 | 29103-HTP-003 HTC-07 | 29103-HTP-003 |  | 113 | 29103-ET-PE1501-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1502-1-PWK-1 | 29103-ET-PE1502-1 | 29103-HTP-003 HTC-06 | 29103-HTP-003 |  | 113 | 29103-ET-PE1502-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1601-1-PWK-1 | 29103-ET-PE1601-1 | 29103-HTP-003 HTC-08 | 29103-HTP-003 |  | 113 | 29103-ET-PE1601-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1601-2-PWK-1 | 29103-ET-PE1601-2 | 29103-HTP-003 HTC-12 | 29103-HTP-003 |  | 113 | 29103-ET-PE1601-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1602-1-PWK-1 | 29103-ET-PE1602-1 | 29103-HTP-003 HTC-15 | 29103-HTP-003 |  | 113 | 29103-ET-PE1602-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1701-1-PWK-1 | 29103-ET-PE1701-1 | 29103-HTP-003 HTC-23 | 29103-HTP-003 |  | 113 | 29103-ET-PE1701-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1701-2-PWK-1 | 29103-ET-PE1701-2 | 29103-HTP-003 HTC-16 | 29103-HTP-003 |  | 113 | 29103-ET-PE1701-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1702-1-PWK-1 | 29103-ET-PE1702-1 | 29103-HTP-003 HTC-20 | 29103-HTP-003 |  | 113 | 29103-ET-PE1702-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1802-2-PWK-1 | 29103-ET-PE1802-2 | 29103-HTP-003 HTC-13 | 29103-HTP-003 |  | 113 | 29103-ET-PE1802-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1803-2-PWK-1 | 29103-ET-PE1803-2 | 29103-HTP-003 HTC-29 | 29103-HTP-003 |  | 113 | 29103-ET-PE1803-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1401-1-PWK-1 | 29103-ET-PG1401-1 | 29103-HTP-003 HTC-35 | 29103-HTP-003 |  | 113 | 29103-ET-PG1401-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1401-2-PWK-1 | 29103-ET-PG1401-2 | 29103-HTP-003 HTC-22 | 29103-HTP-003 |  | 113 | 29103-ET-PG1401-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1501-1-PWK-1 | 29103-ET-PG1501-1 | 29103-HTP-003 HTC-11 | 29103-HTP-003 |  | 113 | 29103-ET-PG1501-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1501-2-PWK-1 | 29103-ET-PG1501-2 | 29103-HTP-003 HTC-28 | 29103-HTP-003 |  | 113 | 29103-ET-PG1501-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1601-1-PWK-1 | 29103-ET-PG1601-1 | 29103-HTP-003 HTC-14 | 29103-HTP-003 |  | 113 | 29103-ET-PG1601-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1601-2-PWK-1 | 29103-ET-PG1601-2 | 29103-HTP-003 HTC-31 | 29103-HTP-003 |  | 113 | 29103-ET-PG1601-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1701-1-PWK-1 | 29103-ET-PG1701-1 | 29103-HTP-003 HTC-21 | 29103-HTP-003 |  | 113 | 29103-ET-PG1701-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1701-2-PWK-1 | 29103-ET-PG1701-2 | 29103-HTP-003 HTC-25 | 29103-HTP-003 |  | 113 | 29103-ET-PG1701-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1303-1-PWK-1 | 29103-ET-ST1303-1 | 29103-AMB-004 | 29103-HTP-003 |  | 113 | 29103-ET-ST1303-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1403-1-PWK-1 | 29103-ET-ST1403-1 | 29103-AMB-004 | 29103-HTP-003 |  | 113 | 29103-ET-ST1403-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1503-1-PWK-1 | 29103-ET-ST1503-1 | 29103-AMB-006 | 29103-HTP-003 |  | 113 | 29103-ET-ST1503-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1603-1-PWK-1 | 29103-ET-ST1603-1 | 29103-AMB-006 | 29103-HTP-003 |  | 113 | 29103-ET-ST1603-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1703-1-PWK-1 | 29103-ET-ST1703-1 | 29103-AMB-006 | 29103-HTP-003 |  | 113 | 29103-ET-ST1703-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
RTD | 29103-ET-P1404-1-R-1 | 29103-ET-P1404-1 | 29103-HTP-003 HTC-34 | PRODUCED EMULSION | 29103-65R-ET-P1404-01-01 | 13.2 | 29103-ET-P1404-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1404-1-R-2 | 29103-ET-P1404-1 | 29103-HTP-003 HTC-01 | PRODUCED EMULSION | 29103-65R-ET-P1404-01-01 | 13.2 | 29103-ET-P1404-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1404-2-R-1 | 29103-ET-P1404-2 | 29103-HTP-003 HTC-26 | PRODUCED EMULSION | 29103-65R-ET-P1404-02-01 | 13.2 | 29103-ET-P1404-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1404-2-R-2 | 29103-ET-P1404-2 | 29103-HTP-003 HTC-03 | PRODUCED EMULSION | 29103-65R-ET-P1404-02-01 | 13.2 | 29103-ET-P1404-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1501-1-R-1 | 29103-ET-P1501-1 | 29103-HTP-003 HTC-04 | PRODUCED EMULSION | 29103-65R-ET-P1501-01-01 | 13.2 | 29103-ET-P1501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1504-1-R-1 | 29103-ET-P1504-1 | 29103-HTP-003 HTC-02 | PRODUCED EMULSION | 29103-65R-ET-P1504-01-01 | 13.2 | 29103-ET-P1504-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1504-1-R-2 | 29103-ET-P1504-1 | 29103-HTP-003 I/O-1-3 | PRODUCED EMULSION | 29103-65R-ET-P1504-01-01 | 13.2 | 29103-ET-P1504-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1504-2-R-1 | 29103-ET-P1504-2 | 29103-HTP-003 HTC-27 | PRODUCED EMULSION | 29103-65R-ET-P1504-02-01 | 13.2 | 29103-ET-P1504-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1504-2-R-2 | 29103-ET-P1504-2 | 29103-HTP-003 HTC-58 | PRODUCED EMULSION | 29103-65R-ET-P1504-02-01 | 13.2 | 29103-ET-P1504-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1601-1-R-1 | 29103-ET-P1601-1 | 29103-HTP-003 HTC-05 | PRODUCED EMULSION | 29103-65R-ET-P1601-01-01 | 13.2 | 29103-ET-P1601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1604-1-R-1 | 29103-ET-P1604-1 | 29103-HTP-003 HTC-09 | PRODUCED EMULSION | 29103-65R-ET-P1604-01-01 | 13.2 | 29103-ET-P1604-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1604-1-R-2 | 29103-ET-P1604-1 | 29103-HTP-003 I/O-1-4 | PRODUCED EMULSION | 29103-65R-ET-P1604-01-01 | 13.2 | 29103-ET-P1604-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1604-2-R-1 | 29103-ET-P1604-2 | 29103-HTP-003 HTC-17 | PRODUCED EMULSION | 29103-65R-ET-P1604-02-01 | 13.2 | 29103-ET-P1604-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1604-2-R-2 | 29103-ET-P1604-2 | 29103-HTP-003 HTC-59 | PRODUCED EMULSION | 29103-65R-ET-P1604-02-01 | 13.2 | 29103-ET-P1604-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1701-1-R-1 | 29103-ET-P1701-1 | 29103-HTP-003 HTC-19 | PRODUCED EMULSION | 29103-65R-ET-P1701-01-01 | 13.2 | 29103-ET-P1701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1704-1-R-1 | 29103-ET-P1704-1 | 29103-HTP-003 HTC-18 | PRODUCED EMULSION | 29103-65R-ET-P1704-01-01 | 13.2 | 29103-ET-P1704-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1704-1-R-2 | 29103-ET-P1704-1 | 29103-HTP-003 I/O-2-1 | PRODUCED EMULSION | 29103-65R-ET-P1704-01-01 | 13.2 | 29103-ET-P1704-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1704-2-R-1 | 29103-ET-P1704-2 | 29103-HTP-003 HTC-32 | PRODUCED EMULSION | 29103-65R-ET-P1704-02-01 | 13.2 | 29103-ET-P1704-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1704-2-R-2 | 29103-ET-P1704-2 | 29103-HTP-003 HTC-60 | PRODUCED EMULSION | 29103-65R-ET-P1704-02-01 | 13.2 | 29103-ET-P1704-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1800-3-R-1 | 29103-ET-P1800-3 | 29103-HTP-003 HTC-24 | PRODUCED EMULSION | 29103-65R-ET-P1800-03-01 | 13.2 | 29103-ET-P1800-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1401-2-R-2 | 29103-ET-PE1401-2 | 29103-HTP-003 I/O-4-3 | PRODUCED EMULSION | 29103-65R-ET-PE1401-02-01 | 13.2 | 29103-ET-PE1401-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1402-1-R-1 | 29103-ET-PE1402-1 | 29103-HTP-003 I/O-4-4 / CB-33 | PRODUCED EMULSION | 29103-4"-PE-1402-DAPCO-64H-ET Rev 1A3 Trace: 29103-ET-PE1402-1-1 | 13.2 | 29103-ET-PE1402-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 5 | [17 empty] | Levy Ostrup | 2026/08/12
RTD | 29103-ET-PE1402-1-R-2 | 29103-ET-PE1402-1 | 29103-HTP-003 I/O-4-4 / CB-33 | PRODUCED EMULSION | 29103-4"-PE-1402-DAPCO-64H-ET Rev 1A3 Trace: 29103-ET-PE1402-1-1 | 13.2 | 29103-ET-PE1402-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 5 | [17 empty] | Levy Ostrup | 2026/08/12
RTD | 29103-ET-PE1501-1-R-1 | 29103-ET-PE1501-1 | 29103-HTP-003 HTC-10 | PRODUCED EMULSION | 29103-65R-ET-PE1501-01-01 | 13.2 | 29103-ET-PE1501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1501-2-R-2 | 29103-ET-PE1501-2 | 29103-HTP-003 I/O-2-2 | PRODUCED EMULSION | 29103-65R-ET-PE1501-02-01 | 13.2 | 29103-ET-PE1501-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1502-1-R-1 | 29103-ET-PE1502-1 | 29103-HTP-003 I/O-2-3 / CB-06 | PRODUCED EMULSION | 29103-4"-PE-1502-DAPCO-64H-ET Rev 1A2 Trace: 29103-ET-PE1502-1-1 | 13.2 | 29103-ET-PE1502-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 5 | [17 empty] | Levy Ostrup | 2026/08/10 | Core markers are correct.
RTD | 29103-ET-PE1502-1-R-2 | 29103-ET-PE1502-1 | 29103-HTP-003 I/O-2-3 / CB-06 | PRODUCED EMULSION | 29103-4"-PE-1502-DAPCO-64H-ET Rev 1A2 Trace: 29103-ET-PE1502-1-1 | 13.2 | 29103-ET-PE1502-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 5 | [17 empty] | Levy Ostrup | 2026/08/10 | Core markers are correct.
RTD | 29103-ET-PE1601-1-R-1 | 29103-ET-PE1601-1 | 29103-HTP-003 HTC-08 | PRODUCED EMULSION | 29103-65R-ET-PE1601-01-01 | 13.2 | 29103-ET-PE1601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1601-2-R-2 | 29103-ET-PE1601-2 | 29103-HTP-003 I/O-2-4 | PRODUCED EMULSION | 29103-65R-ET-PE1601-02-01 | 13.2 | 29103-ET-PE1601-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1602-1-R-1 | 29103-ET-PE1602-1 | 29103-HTP-003 I/O-3-1 / CB-15 | PRODUCED EMULSION | 29103-4"-PE-1602-DAPCO-64H-ET Rev 1A2 Trace: 29103-ET-PE1602-1-1 | 13.2 | 29103-ET-PE1602-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 6 | [17 empty] | Levy Ostrup | 2026/08/10 | Has been terminated, SS tag is installed but upside down. ¦ Core markers are 29103HTP003HTC15-P-H and 29103HTP003HTC15-P-N
RTD | 29103-ET-PE1602-1-R-2 | 29103-ET-PE1602-1 | 29103-HTP-003 I/O-3-1 / CB-15 | PRODUCED EMULSION | 29103-4"-PE-1602-DAPCO-64H-ET Rev 1A2 Trace: 29103-ET-PE1602-1-1 | 13.2 | 29103-ET-PE1602-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 6 | [17 empty] | Levy Ostrup | 2026/08/10 | Has been terminated, SS tag is installed but upside down. ¦ Core markers are 29103HTP003HTC15-P-H and 29103HTP003HTC15-P-N
RTD | 29103-ET-PE1701-1-R-1 | 29103-ET-PE1701-1 | 29103-HTP-003 HTC-23 | PRODUCED EMULSION | 29103-65R-ET-PE1701-01-01 | 13.2 | 29103-ET-PE1701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1701-2-R-2 | 29103-ET-PE1701-2 | 29103-HTP-003 I/O-3-2 | PRODUCED EMULSION | 29103-65R-ET-PE1701-02-01 | 13.2 | 29103-ET-PE1701-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1702-1-R-1 | 29103-ET-PE1702-1 | 29103-HTP-003 HTC-20 | PRODUCED EMULSION | 29103-65R-ET-PE1702-01-01 | 13.2 | 29103-ET-PE1702-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1702-1-R-2 | 29103-ET-PE1702-1 | 29103-HTP-003 I/O-3-3 | PRODUCED EMULSION | 29103-65R-ET-PE1702-01-01 | 13.2 | 29103-ET-PE1702-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1802-2-R-1 | 29103-ET-PE1802-2 | 29103-HTP-003 HTC-13 | PRODUCED EMULSION | 29103-65R-ET-PE1802-02-01 | 13.2 | 29103-ET-PE1802-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1803-2-R-1 | 29103-ET-PE1803-2 | 29103-HTP-003 HTC-29 | PRODUCED EMULSION | 29103-65R-ET-PE1803-02-01 | 13.2 | 29103-ET-PE1803-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1401-1-R-1 | 29103-ET-PG1401-1 | 29103-HTP-003 HTC-35 | PRODUCED GAS | 29103-65R-ET-PG1401-01-01 | 13.2 | 29103-ET-PG1401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1401-1-R-2 | 29103-ET-PG1401-1 | 29103-HTP-003 HTC-37 | PRODUCED GAS | 29103-65R-ET-PG1401-01-01 | 13.2 | 29103-ET-PG1401-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1401-2-R-1 | 29103-ET-PG1401-2 | 29103-HTP-003 HTC-22 | PRODUCED GAS | 29103-65R-ET-PG1401-02-01 | 13.2 | 29103-ET-PG1401-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1501-1-R-1 | 29103-ET-PG1501-1 | 29103-HTP-003 HTC-11 | PRODUCED GAS | 29103-65R-ET-PG1501-01-01 | 13.2 | 29103-ET-PG1501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1501-1-R-2 | 29103-ET-PG1501-1 | 29103-HTP-003 I/O-3-4 | PRODUCED GAS | 29103-65R-ET-PG1501-01-01 | 13.2 | 29103-ET-PG1501-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1501-2-R-1 | 29103-ET-PG1501-2 | 29103-HTP-003 HTC-28 | PRODUCED GAS | 29103-65R-ET-PG1501-02-01 | 13.2 | 29103-ET-PG1501-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1601-1-R-1 | 29103-ET-PG1601-1 | 29103-HTP-003 HTC-14 | PRODUCED GAS | 29103-65R-ET-PG1601-01-01 | 13.2 | 29103-ET-PG1601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1601-1-R-2 | 29103-ET-PG1601-1 | 29103-HTP-003 I/O-4-1 | PRODUCED GAS | 29103-65R-ET-PG1601-01-01 | 13.2 | 29103-ET-PG1601-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1601-2-R-1 | 29103-ET-PG1601-2 | 29103-HTP-003 HTC-31 | PRODUCED GAS | 29103-65R-ET-PG1601-02-01 | 13.2 | 29103-ET-PG1601-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1701-1-R-1 | 29103-ET-PG1701-1 | 29103-HTP-003 HTC-21 | PRODUCED GAS | 29103-65R-ET-PG1701-01-01 | 13.2 | 29103-ET-PG1701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1701-1-R-2 | 29103-ET-PG1701-1 | 29103-HTP-003 I/O-4-2 | PRODUCED GAS | 29103-65R-ET-PG1701-01-01 | 13.2 | 29103-ET-PG1701-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1701-2-R-1 | 29103-ET-PG1701-2 | 29103-HTP-003 HTC-25 | PRODUCED GAS | 29103-65R-ET-PG1701-02-01 | 13.2 | 29103-ET-PG1701-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD Cable | 29103-ET-P1404-1-R-1 | 29103-ET-P1404-1 | 29103-HTP-003 HTC-34 | 29103-HTP-003 |  | 113 | 29103-ET-P1404-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1404-1-R-2 | 29103-ET-P1404-1 | 29103-HTP-003 HTC-01 | 29103-HTP-003 |  | 113 | 29103-ET-P1404-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1404-2-R-1 | 29103-ET-P1404-2 | 29103-HTP-003 HTC-26 | 29103-HTP-003 |  | 113 | 29103-ET-P1404-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1404-2-R-2 | 29103-ET-P1404-2 | 29103-HTP-003 HTC-03 | 29103-HTP-003 |  | 113 | 29103-ET-P1404-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1501-1-R-1 | 29103-ET-P1501-1 | 29103-HTP-003 HTC-04 | 29103-HTP-003 |  | 113 | 29103-ET-P1501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1504-1-R-1 | 29103-ET-P1504-1 | 29103-HTP-003 HTC-02 | 29103-HTP-003 |  | 113 | 29103-ET-P1504-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1504-1-R-2 | 29103-ET-P1504-1 | 29103-HTP-003 I/O-1-3 | 29103-HTP-003 |  | 113 | 29103-ET-P1504-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1504-2-R-1 | 29103-ET-P1504-2 | 29103-HTP-003 HTC-27 | 29103-HTP-003 |  | 113 | 29103-ET-P1504-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1504-2-R-2 | 29103-ET-P1504-2 | 29103-HTP-003 HTC-58 | 29103-HTP-003 |  | 113 | 29103-ET-P1504-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1601-1-R-1 | 29103-ET-P1601-1 | 29103-HTP-003 HTC-05 | 29103-HTP-003 |  | 113 | 29103-ET-P1601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1604-1-R-1 | 29103-ET-P1604-1 | 29103-HTP-003 HTC-09 | 29103-HTP-003 |  | 113 | 29103-ET-P1604-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1604-1-R-2 | 29103-ET-P1604-1 | 29103-HTP-003 I/O-1-4 | 29103-HTP-003 |  | 113 | 29103-ET-P1604-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1604-2-R-1 | 29103-ET-P1604-2 | 29103-HTP-003 HTC-17 | 29103-HTP-003 |  | 113 | 29103-ET-P1604-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1604-2-R-2 | 29103-ET-P1604-2 | 29103-HTP-003 HTC-59 | 29103-HTP-003 |  | 113 | 29103-ET-P1604-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1701-1-R-1 | 29103-ET-P1701-1 | 29103-HTP-003 HTC-19 | 29103-HTP-003 |  | 113 | 29103-ET-P1701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1704-1-R-1 | 29103-ET-P1704-1 | 29103-HTP-003 HTC-18 | 29103-HTP-003 |  | 113 | 29103-ET-P1704-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1704-1-R-2 | 29103-ET-P1704-1 | 29103-HTP-003 I/O-2-1 | 29103-HTP-003 |  | 113 | 29103-ET-P1704-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1704-2-R-1 | 29103-ET-P1704-2 | 29103-HTP-003 HTC-32 | 29103-HTP-003 |  | 113 | 29103-ET-P1704-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1704-2-R-2 | 29103-ET-P1704-2 | 29103-HTP-003 HTC-60 | 29103-HTP-003 |  | 113 | 29103-ET-P1704-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1800-3-R-1 | 29103-ET-P1800-3 | 29103-HTP-003 HTC-24 | 29103-HTP-003 |  | 113 | 29103-ET-P1800-3-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1401-2-R-2 | 29103-ET-PE1401-2 | 29103-HTP-003 I/O-4-3 | 29103-HTP-003 |  | 113 | 29103-ET-PE1401-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1402-1-R-1 | 29103-ET-PE1402-1 | 29103-HTP-003 HTC-33 | 29103-HTP-003 |  | 113 | 29103-ET-PE1402-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1402-1-R-2 | 29103-ET-PE1402-1 | 29103-HTP-003 I/O-4-4 | 29103-HTP-003 |  | 113 | 29103-ET-PE1402-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1501-1-R-1 | 29103-ET-PE1501-1 | 29103-HTP-003 HTC-10 | 29103-HTP-003 |  | 113 | 29103-ET-PE1501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1501-2-R-2 | 29103-ET-PE1501-2 | 29103-HTP-003 I/O-2-2 | 29103-HTP-003 |  | 113 | 29103-ET-PE1501-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1502-1-R-1 | 29103-ET-PE1502-1 | 29103-HTP-003 HTC-06 | 29103-HTP-003 |  | 113 | 29103-ET-PE1502-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1502-1-R-2 | 29103-ET-PE1502-1 | 29103-HTP-003 I/O-2-3 | 29103-HTP-003 |  | 113 | 29103-ET-PE1502-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1601-1-R-1 | 29103-ET-PE1601-1 | 29103-HTP-003 HTC-08 | 29103-HTP-003 |  | 113 | 29103-ET-PE1601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1601-2-R-2 | 29103-ET-PE1601-2 | 29103-HTP-003 I/O-2-4 | 29103-HTP-003 |  | 113 | 29103-ET-PE1601-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1602-1-R-1 | 29103-ET-PE1602-1 | 29103-HTP-003 HTC-15 | 29103-HTP-003 |  | 113 | 29103-ET-PE1602-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1602-1-R-2 | 29103-ET-PE1602-1 | 29103-HTP-003 I/O-3-1 | 29103-HTP-003 |  | 113 | 29103-ET-PE1602-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1701-1-R-1 | 29103-ET-PE1701-1 | 29103-HTP-003 HTC-23 | 29103-HTP-003 |  | 113 | 29103-ET-PE1701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1701-2-R-2 | 29103-ET-PE1701-2 | 29103-HTP-003 I/O-3-2 | 29103-HTP-003 |  | 113 | 29103-ET-PE1701-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1702-1-R-1 | 29103-ET-PE1702-1 | 29103-HTP-003 HTC-20 | 29103-HTP-003 |  | 113 | 29103-ET-PE1702-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1702-1-R-2 | 29103-ET-PE1702-1 | 29103-HTP-003 I/O-3-3 | 29103-HTP-003 |  | 113 | 29103-ET-PE1702-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1802-2-R-1 | 29103-ET-PE1802-2 | 29103-HTP-003 HTC-13 | 29103-HTP-003 |  | 113 | 29103-ET-PE1802-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1803-2-R-1 | 29103-ET-PE1803-2 | 29103-HTP-003 HTC-29 | 29103-HTP-003 |  | 113 | 29103-ET-PE1803-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1401-1-R-1 | 29103-ET-PG1401-1 | 29103-HTP-003 HTC-35 | 29103-HTP-003 |  | 113 | 29103-ET-PG1401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1401-1-R-2 | 29103-ET-PG1401-1 | 29103-HTP-003 HTC-37 | 29103-HTP-003 |  | 113 | 29103-ET-PG1401-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1401-2-R-1 | 29103-ET-PG1401-2 | 29103-HTP-003 HTC-22 | 29103-HTP-003 |  | 113 | 29103-ET-PG1401-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1501-1-R-1 | 29103-ET-PG1501-1 | 29103-HTP-003 HTC-11 | 29103-HTP-003 |  | 113 | 29103-ET-PG1501-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1501-1-R-2 | 29103-ET-PG1501-1 | 29103-HTP-003 I/O-3-4 | 29103-HTP-003 |  | 113 | 29103-ET-PG1501-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1501-2-R-1 | 29103-ET-PG1501-2 | 29103-HTP-003 HTC-28 | 29103-HTP-003 |  | 113 | 29103-ET-PG1501-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1601-1-R-1 | 29103-ET-PG1601-1 | 29103-HTP-003 HTC-14 | 29103-HTP-003 |  | 113 | 29103-ET-PG1601-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1601-1-R-2 | 29103-ET-PG1601-1 | 29103-HTP-003 I/O-4-1 | 29103-HTP-003 |  | 113 | 29103-ET-PG1601-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1601-2-R-1 | 29103-ET-PG1601-2 | 29103-HTP-003 HTC-31 | 29103-HTP-003 |  | 113 | 29103-ET-PG1601-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1701-1-R-1 | 29103-ET-PG1701-1 | 29103-HTP-003 HTC-21 | 29103-HTP-003 |  | 113 | 29103-ET-PG1701-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1701-1-R-2 | 29103-ET-PG1701-1 | 29103-HTP-003 I/O-4-2 | 29103-HTP-003 |  | 113 | 29103-ET-PG1701-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1701-2-R-1 | 29103-ET-PG1701-2 | 29103-HTP-003 HTC-25 | 29103-HTP-003 |  | 113 | 29103-ET-PG1701-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-004 |  | 29103-HTP-003 HTC-30 | 29103-HTP-003 |  | 113 | 29103-RJB-004.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-005 |  | 29103-HTP-003 HTC-07 | 29103-HTP-003 |  | 113 | 29103-RJB-005.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-006 |  | 29103-HTP-003 HTC-12 | 29103-HTP-003 |  | 113 | 29103-RJB-006.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-007 |  | 29103-HTP-003 HTC-16 | 29103-HTP-003 |  | 113 | 29103-RJB-007.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup

## 29103-HTP-002
29103-HTP-002
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29103-ET-FG1101-1-1 | 29103-ET-FG1101-1 | 29103-AMB-001 | 29103-FG-1101 | 29103-65R-ET-FG1101-01-01 | 13.1 | 29103-ET-FG1101-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 24.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1101-1-2 | 29103-ET-FG1101-1 | 29103-AMB-001 |  | 29103-65R-ET-FG1101-01-01 | 13.1 | 29103-ET-FG1101-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 1.2 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1103-1-1 | 29103-ET-FG1103-1 | 29103-AMB-001 | 29103-FG-1103 | 29103-65R-ET-FG1103-01-01 | 13.1 | 29103-ET-FG1103-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 12.8 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1103-1-2 | 29103-ET-FG1103-1 | 29103-AMB-001 | 29103-FG-1103 | 29103-65R-ET-FG1103-01-01 | 13.1 | 29103-ET-FG1103-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 14.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1103-1-3 | 29103-ET-FG1103-1 | 29103-AMB-001 |  | 29103-65R-ET-FG1103-01-01 | 13.1 | 29103-ET-FG1103-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1103-1-4 | 29103-ET-FG1103-1 | 29103-AMB-001 |  | 29103-65R-ET-FG1103-01-01 | 13.1 | 29103-ET-FG1103-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1105-1-1 | 29103-ET-FG1105-1 | 29103-AMB-002 | 29103-FG-1106, 29103-FG-1105 | 29103-65R-ET-FG1105-01-01 | 13.1 | 29103-ET-FG1105-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 344 Ω | 2026-05-17 | [12 empty] | D/32SA2600/16.9M/230/277/1.2M/LS23A/X/N12 | 16.9 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1201-1-1 | 29103-ET-FG1201-1 | 29103-AMB-001 | 29103-FG-1201 | 29103-65R-ET-FG1201-01-01 | 13.1 | 29103-ET-FG1201-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 24.3 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1203-1-1 | 29103-ET-FG1203-1 | 29103-AMB-001 | 29103-FG-1203 | 29103-65R-ET-FG1203-01-01 | 13.1 | 29103-ET-FG1203-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 11.6 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1203-1-2 | 29103-ET-FG1203-1 | 29103-AMB-001 | 29103-FG-1203 | 29103-65R-ET-FG1203-01-01 | 13.1 | 29103-ET-FG1203-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.3 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1203-1-3 | 29103-ET-FG1203-1 | 29103-AMB-001 |  | 29103-65R-ET-FG1203-01-01 | 13.1 | 29103-ET-FG1203-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1203-1-4 | 29103-ET-FG1203-1 | 29103-AMB-001 |  | 29103-65R-ET-FG1203-01-01 | 13.1 | 29103-ET-FG1203-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1301-1-1 | 29103-ET-FG1301-1 | 29103-AMB-003 | 29103-FG-1301 | 29103-65R-ET-FG1301-01-01 | 13.1 | 29103-ET-FG1301-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 23.3 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1303-1-1 | 29103-ET-FG1303-1 | 29103-AMB-003 | 29103-FG-1303 | 29103-65R-ET-FG1303-01-01 | 13.1 | 29103-ET-FG1303-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1303-1-2 | 29103-ET-FG1303-1 | 29103-AMB-003 | 29103-FG-1303 | 29103-65R-ET-FG1303-01-01 | 13.1 | 29103-ET-FG1303-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 14.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1303-1-3 | 29103-ET-FG1303-1 | 29103-AMB-003 |  | 29103-65R-ET-FG1303-01-01 | 13.1 | 29103-ET-FG1303-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1303-1-4 | 29103-ET-FG1303-1 | 29103-AMB-003 |  | 29103-65R-ET-FG1303-01-01 | 13.1 | 29103-ET-FG1303-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1401-1-1 | 29103-ET-FG1401-1 | 29103-AMB-003 | 29103-FG-1401 | 29103-65R-ET-FG1401-01-01 | 13.1 | 29103-ET-FG1401-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 24.4 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1403-1-1 | 29103-ET-FG1403-1 | 29103-AMB-003 | 29103-FG-1403 | 29103-65R-ET-FG1403-01-01 | 13.1 | 29103-ET-FG1403-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1403-1-2 | 29103-ET-FG1403-1 | 29103-AMB-003 | 29103-FG-1403 | 29103-65R-ET-FG1403-01-01 | 13.1 | 29103-ET-FG1403-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.5 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1403-1-3 | 29103-ET-FG1403-1 | 29103-AMB-003 |  | 29103-65R-ET-FG1403-01-01 | 13.1 | 29103-ET-FG1403-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 6.1 m m | Levy Ostrup
EHT Trace | 29103-ET-FG1403-1-4 | 29103-ET-FG1403-1 | 29103-AMB-003 |  | 29103-65R-ET-FG1403-01-01 | 13.1 | 29103-ET-FG1403-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR2-CT | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1101-1-1 | 29103-ET-P1101-1 | HTC-37 / CB-37 | 29103-P-1101 | 29103-65R-ET-P1101-01-01 | 13.1 | 29103-ET-P1101-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.5M/1007/166/1.2M/LS23A/X/N12/XNF | 20.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P1101-1-2 | 29103-ET-P1101-1 | HTC-37 / CB-37 | 29103-P-1101 | 29103-65R-ET-P1101-01-01 | 13.1 | 29103-ET-P1101-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.8M/678/111/1.2M/LS23A/X/N12/XMN | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1104-1-1 | 29103-ET-P1104-1 | HTC-35 / CB-35 | 29103-PE-1101, 29103-P-1104 | 29103-65R-ET-P1104-01-01 | 13.1 | 29103-ET-P1104-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1104-1-2 | 29103-ET-P1104-1 | HTC-35 / CB-35 | 29103-P-1104 | 29103-65R-ET-P1104-01-01 | 13.1 | 29103-ET-P1104-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.7 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/8M/461/78.9/1.2M/LS23A/X/N12/XNF | 8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1104-1-3 | 29103-ET-P1104-1 | HTC-35 / CB-35 | 29103-P-1104 | 29103-65R-ET-P1104-01-01 | 13.1 | 29103-ET-P1104-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.3 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/403/69/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1104-1-4 | 29103-ET-P1104-1 | HTC-35 / CB-35 | 29103-P-1104 | 29103-65R-ET-P1104-01-01 | 13.1 | 29103-ET-P1104-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 21.1 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/755/129/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1104-2-1 | 29103-ET-P1104-2 | HTC-40 / CB-40 | 29103-P-1104, 29103-FG-1102 | 29103-65R-ET-P1104-02-01 | 13.1 | 29103-ET-P1104-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 373.2 Ω | 2026-05-17 | [12 empty] | D/32SF1180/6.2M/207/277/1.2M/LS23A/X/N12 | 6.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P1201-1-1 | 29103-ET-P1201-1 | HTC-39 / CB-39 | 29103-P-1201 | 29103-65R-ET-P1201-01-01 | 13.1 | 29103-ET-P1201-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.6M/1001/165/1.2M/LS23A/X/N12/XNF | 20.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P1201-1-2 | 29103-ET-P1201-1 | HTC-39 / CB-39 | 29103-P-1201 | 29103-65R-ET-P1201-01-01 | 13.1 | 29103-ET-P1201-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.9M/676/112/1.2M/LS23A/X/N12/XMN | 13.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1204-1-1 | 29103-ET-P1204-1 | HTC-27 / CB-27 | 29103-PE-1201, 29103-P-1204 | 29103-65R-ET-P1204-01-01 | 13.1 | 29103-ET-P1204-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1204-1-2 | 29103-ET-P1204-1 | HTC-27 / CB-27 | 29103-P-1204 | 29103-65R-ET-P1204-01-01 | 13.1 | 29103-ET-P1204-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 10.5 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/6.5M/416/67.7/1.2M/LS23A/X/N12/XNF | 6.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P1204-1-3 | 29103-ET-P1204-1 | HTC-27 / CB-27 | 29103-P-1204 | 29103-65R-ET-P1204-01-01 | 13.1 | 29103-ET-P1204-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.6 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/448/72.9/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1204-1-4 | 29103-ET-P1204-1 | HTC-27 / CB-27 | 29103-P-1204 | 29103-65R-ET-P1204-01-01 | 13.1 | 29103-ET-P1204-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 20.9 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/838/136/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1204-2-1 | 29103-ET-P1204-2 | HTC-29 / CB-29 | 29103-P-1204, 29103-FG-1202 | 29103-65R-ET-P1204-02-01 | 13.1 | 29103-ET-P1204-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 262.1 Ω | 2026-05-17 | [12 empty] | D/32SF1110/7M/299/277/1.2M/LS23A/X/N12 | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1301-1-1 | 29103-ET-P1301-1 | HTC-38 / CB-38 | 29103-P-1301 | 29103-65R-ET-P1301-01-01 | 13.1 | 29103-ET-P1301-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.5M/1007/166/1.2M/LS23A/X/N12/XNF | 20.5 m m | Levy Ostrup
EHT Trace | 29103-ET-P1301-1-2 | 29103-ET-P1301-1 | HTC-38 / CB-38 | 29103-P-1301 | 29103-65R-ET-P1301-01-01 | 13.1 | 29103-ET-P1301-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.8M/678/111/1.2M/LS23A/X/N12/XMN | 13.8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1304-1-1 | 29103-ET-P1304-1 | HTC-09 / CB-09 | 29103-PE-1301, 29103-P-1304 | 29103-65R-ET-P1304-01-01 | 13.1 | 29103-ET-P1304-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SA2200/20.9M/554/277/1.2M/LS23A/X/N12 | 20.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1304-1-2 | 29103-ET-P1304-1 | HTC-09 / CB-09 | 29103-P-1304 | 29103-65R-ET-P1304-01-01 | 13.1 | 29103-ET-P1304-1-2.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 12.8 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/8M/461/78.9/1.2M/LS23A/X/N12/XNF | 8 m m | Levy Ostrup
EHT Trace | 29103-ET-P1304-1-3 | 29103-ET-P1304-1 | HTC-09 / CB-09 | 29103-P-1304 | 29103-65R-ET-P1304-01-01 | 13.1 | 29103-ET-P1304-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 11.4 Ω | 2026-05-17 | [12 empty] | E/32SQ3472/7M/403/69/1.2M/LS23A/X/N12/XMF | 7 m m | Levy Ostrup
EHT Trace | 29103-ET-P1304-1-4 | 29103-ET-P1304-1 | HTC-09 / CB-09 | 29103-P-1304 | 29103-65R-ET-P1304-01-01 | 13.1 | 29103-ET-P1304-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 21 Ω | 2026-05-17 | [12 empty] | D/32SQ3472/13.1M/755/129/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1304-2-1 | 29103-ET-P1304-2 | HTC-19 / CB-19 | 29103-P-1304, 29103-FG-1302 | 29103-65R-ET-P1304-02-01 | 13.1 | 29103-ET-P1304-2-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 374.3 Ω | 2026-05-17 | [12 empty] | D/32SF1180/6.2M/207/277/1.2M/LS23A/X/N12 | 6.2 m m | Levy Ostrup
EHT Trace | 29103-ET-P1401-1-1 | 29103-ET-P1401-1 | HTC-05 / CB-05 | 29103-P-1401 | 29103-65R-ET-P1401-01-01 | 13.1 | 29103-ET-P1401-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3374/20.6M/1001/165/1.2M/LS23A/X/N12/XNF | 20.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P1401-1-2 | 29103-ET-P1401-1 | HTC-05 / CB-05 | 29103-P-1401 | 29103-65R-ET-P1401-01-01 | 13.1 | 29103-ET-P1401-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3374/13.9M/676/112/1.2M/LS23A/X/N12/XMN | 13.9 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-1-1 | 29103-ET-P1800-1 | HTC-26 / CB-26 | 29103-P-1800 | 29103-65R-ET-P1800-01-01 | 13.1 | 29103-ET-P1800-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/58.6M/2332/198/2.1M/LS23A/X/N12 | 58.6 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-1-2 | 29103-ET-P1800-1 | HTC-26 / CB-26 | 29103-P-1800 | 29103-65R-ET-P1800-01-01 | 13.1 | 29103-ET-P1800-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/23.3M/927/78.8/2.1M/LS23A/X/N12 | 23.3 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-2-1 | 29103-ET-P1800-2 | HTC-16 / CB-16 | 29103-P-1800 | 29103-65R-ET-P1800-02-01 | 13.1 | 29103-ET-P1800-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/47.1M/2553/207/2.1M/LS23A/X/N12 | 47.1 m m | Levy Ostrup
EHT Trace | 29103-ET-P1800-2-2 | 29103-ET-P1800-2 | HTC-16 / CB-16 | 29103-P-1800 | 29103-65R-ET-P1800-02-01 | 13.1 | 29103-ET-P1800-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/15.9M/862/69.9/2.1M/LS23A/X/N12 | 15.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1101-1-1 | 29103-ET-PE1101-1 | HTC-25 / CB-25 | 29103-PE-1101 | 29103-65R-ET-PE1101-01-01 | 13.1 | 29103-ET-PE1101-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.8M/269/277/1.2M/LS23A/X/N12 | 7.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1101-1-2 | 29103-ET-PE1101-1 | HTC-25 / CB-25 | 29103-PE-1101 | 29103-65R-ET-PE1101-01-01 | 13.1 | 29103-ET-PE1101-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/9.5M/505/89.8/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1101-1-3 | 29103-ET-PE1101-1 | HTC-25 / CB-25 | 29103-PE-1101 | 29103-65R-ET-PE1101-01-01 | 13.1 | 29103-ET-PE1101-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/351/62.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1101-1-4 | 29103-ET-PE1101-1 | HTC-25 / CB-25 | 29103-PE-1101 | 29103-65R-ET-PE1101-01-01 | 13.1 | 29103-ET-PE1101-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.2M/702/125/1.2M/LS23A/X/N12/XMN | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1101-2-1 | 29103-ET-PE1101-2 | HTC-24 / CB-24 | 29103-PE-1101 | 29103-65R-ET-PE1101-02-01 | 13.1 | 29103-ET-PE1101-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.5M/2063/277/1.2M/LS23A/X/N12 | 52.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1101-2-2 | 29103-ET-PE1101-2 | HTC-24 / CB-24 | 29103-PE-1101 | 29103-65R-ET-PE1101-02-01 | 13.1 | 29103-ET-PE1101-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.4M/694/277/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1102-1-1 | 29103-ET-PE1102-1 | HTC-23 / CB-23 | 29103-PE-1103, 29103-PE-1102 | 29103-65R-ET-PE1102-01-01 | 13.1 | 29103-ET-PE1102-1-1.pdf | YES | YES | NO | YES | NO | N/A | N/A | N/A | N/A | YES | NO | 3 |  |  |  | 550 MΩ | 44.7 Ω | 2026-08-12 | [9 empty] | D/32SQ3374/34.9M/1658/277/1.2M/LS23A/X/N12 | 34.9 m m | Levy Ostrup |  | No core markers for the RTD.
EHT Trace | 29103-ET-PE1201-1-1 | 29103-ET-PE1201-1 | HTC-22 / CB-22 | 29103-PE-1201 | 29103-65R-ET-PE1201-01-01 | 13.1 | 29103-ET-PE1201-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.5M/280/277/1.2M/LS23A/X/N12 | 7.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1201-1-2 | 29103-ET-PE1201-1 | HTC-22 / CB-22 | 29103-PE-1201 | 29103-65R-ET-PE1201-01-01 | 13.1 | 29103-ET-PE1201-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/10.8M/522/97.1/1.2M/LS23A/X/N12/XNF | 10.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1201-1-3 | 29103-ET-PE1201-1 | HTC-22 / CB-22 | 29103-PE-1201 | 29103-65R-ET-PE1201-01-01 | 13.1 | 29103-ET-PE1201-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/319/59.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1201-1-4 | 29103-ET-PE1201-1 | HTC-22 / CB-22 | 29103-PE-1201 | 29103-65R-ET-PE1201-01-01 | 13.1 | 29103-ET-PE1201-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.4M/647/121/1.2M/LS23A/X/N12/XMN | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1201-2-1 | 29103-ET-PE1201-2 | HTC-20 / CB-20 | 29103-PE-1201 | 29103-65R-ET-PE1201-02-01 | 13.1 | 29103-ET-PE1201-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.1M/2079/277/1.2M/LS23A/X/N12 | 52.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1201-2-2 | 29103-ET-PE1201-2 | HTC-20 / CB-20 | 29103-PE-1201 | 29103-65R-ET-PE1201-02-01 | 13.1 | 29103-ET-PE1201-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.2M/701/277/1.2M/LS23A/X/N12 | 29.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1202-1-1 | 29103-ET-PE1202-1 | HTC-18 / CB-18 | 29103-PE-1203, 29103-PE-1202 | 29103-65R-ET-PE1202-01-01 | 13.1 | 29103-ET-PE1202-1-1.pdf | YES | YES | NO | YES | NO | N/A | N/A | N/A | N/A | YES | NO | 3 |  |  |  | 550 MΩ | 44.7 Ω | 2026-08-12 | [9 empty] | D/32SQ3374/35.4M/1635/277/1.2M/LS23A/X/N12 | 35.4 m m | Levy Ostrup |  | No stainless steel tags for the JB or RTD.
EHT Trace | 29103-ET-PE1301-1-1 | 29103-ET-PE1301-1 | HTC-10 / CB-10 | 29103-PE-1301 | 29103-65R-ET-PE1301-01-01 | 13.1 | 29103-ET-PE1301-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.8M/269/277/1.2M/LS23A/X/N12 | 7.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1301-1-2 | 29103-ET-PE1301-1 | HTC-10 / CB-10 | 29103-PE-1301 | 29103-65R-ET-PE1301-01-01 | 13.1 | 29103-ET-PE1301-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/9.5M/505/89.8/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1301-1-3 | 29103-ET-PE1301-1 | HTC-10 / CB-10 | 29103-PE-1301 | 29103-65R-ET-PE1301-01-01 | 13.1 | 29103-ET-PE1301-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/351/62.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1301-1-4 | 29103-ET-PE1301-1 | HTC-10 / CB-10 | 29103-PE-1301 | 29103-65R-ET-PE1301-01-01 | 13.1 | 29103-ET-PE1301-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.2M/702/125/1.2M/LS23A/X/N12/XMN | 13.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1301-2-1 | 29103-ET-PE1301-2 | HTC-07 / CB-07 | 29103-PE-1301 | 29103-65R-ET-PE1301-02-01 | 13.1 | 29103-ET-PE1301-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3200/52.5M/2063/277/1.2M/LS23A/X/N12 | 52.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1301-2-2 | 29103-ET-PE1301-2 | HTC-07 / CB-07 | 29103-PE-1301 | 29103-65R-ET-PE1301-02-01 | 13.1 | 29103-ET-PE1301-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/29.4M/694/277/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1302-1-1 | 29103-ET-PE1302-1 | HTC-06 / CB-06 | 29103-PE-1303, 29103-PE-1302 | 29103-65R-ET-PE1302-01-01 | 13.1 | 29103-ET-PE1302-1-1.pdf | YES | YES | NO | YES | NO | N/A | N/A | N/A | N/A | YES | NO | 3 |  |  |  | 550 MΩ | 44.9 Ω | 2026-08-12 | [9 empty] | D/32SQ3374/34.9M/1658/277/1.2M/LS23A/X/N12 | 34.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1401-1-1 | 29103-ET-PE1401-1 | HTC-04 / CB-04 | 29103-PE-1401 | 29103-65R-ET-PE1401-01-01 | 13.1 | 29103-ET-PE1401-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SF1110/7.5M/280/277/1.2M/LS23A/X/N12 | 7.5 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1401-1-2 | 29103-ET-PE1401-1 | HTC-04 / CB-04 | 29103-PE-1401 | 29103-65R-ET-PE1401-01-01 | 13.1 | 29103-ET-PE1401-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/10.8M/522/97.1/1.2M/LS23A/X/N12/XNF | 10.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1401-1-3 | 29103-ET-PE1401-1 | HTC-04 / CB-04 | 29103-PE-1401 | 29103-65R-ET-PE1401-01-01 | 13.1 | 29103-ET-PE1401-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3472/6.6M/319/59.4/1.2M/LS23A/X/N12/XMF | 6.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1401-1-4 | 29103-ET-PE1401-1 | HTC-04 / CB-04 | 29103-PE-1401 | 29103-65R-ET-PE1401-01-01 | 13.1 | 29103-ET-PE1401-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/13.4M/647/121/1.2M/LS23A/X/N12/XMN | 13.4 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-1-1 | 29103-ET-PE1802-1 | HTC-17 / CB-17 | 29103-PE-1802 | 29103-65R-ET-PE1802-01-01 | 13.1 | 29103-ET-PE1802-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SP4734/24.2M/2105/126/2.1-1.2M/LS23A/X/N12/XNF | 24.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-1-2 | 29103-ET-PE1802-1 | HTC-17 / CB-17 | 29103-PE-1802 | 29103-65R-ET-PE1802-01-01 | 13.1 | 29103-ET-PE1802-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SP4734/8.9M/774/46.2/1.2M/LS23A/X/N12/XMF | 8.9 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1802-1-3 | 29103-ET-PE1802-1 | HTC-17 / CB-17 | 29103-PE-1802 | 29103-65R-ET-PE1802-01-01 | 13.1 | 29103-ET-PE1802-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/20.3M/1766/105/1.2M/LS23A/X/N12/XMN | 20.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-1-1 | 29103-ET-PE1803-1 | HTC-21 / CB-21 | 29103-PE-1803 | 29103-65R-ET-PE1803-01-01 | 13.1 | 29103-ET-PE1803-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3100/9.7M/437/38.8/1.2M/LS23A/X/N12/XNF | 9.7 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-1-2 | 29103-ET-PE1803-1 | HTC-21 / CB-21 | 29103-PE-1803 | 29103-65R-ET-PE1803-01-01 | 13.1 | 29103-ET-PE1803-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/26.3M/1186/105/1.2M/LS23A/X/N12/XMN | 26.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-1-3 | 29103-ET-PE1803-1 | HTC-21 / CB-21 | 29103-PE-1803 | 29103-65R-ET-PE1803-01-01 | 13.1 | 29103-ET-PE1803-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SQ3100/22.1M/997/88.3/1.2M/LS23A/X/N12/XNF | 22.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PE1803-1-4 | 29103-ET-PE1803-1 | HTC-21 / CB-21 | 29103-PE-1803 | 29103-65R-ET-PE1803-01-01 | 13.1 | 29103-ET-PE1803-1-4.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/11.2M/505/44.8/1.2M/LS23A/X/N12/XMN | 11.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1101-1-1 | 29103-ET-PG1101-1 | HTC-15 / CB-15 | 29103-PG-1101, 29103-PE-1102, 29103-P-1100 | 29103-65R-ET-PG1101-01-01 | 13.1 | 29103-ET-PG1101-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/90M/3006/277/1.2M/LS23A/X/N12 | 90 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1101-2-1 | 29103-ET-PG1101-2 | HTC-14 / CB-14 | 29103-PG-1101 | 29103-65R-ET-PG1101-02-01 | 13.1 | 29103-ET-PG1101-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/9.2M/409/93.3/1.2M/LS23A/X/N12/XNF | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1101-2-2 | 29103-ET-PG1101-2 | HTC-14 / CB-14 | 29103-PG-1101 | 29103-65R-ET-PG1101-02-01 | 13.1 | 29103-ET-PG1101-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/6.3M/280/63.9/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1101-2-3 | 29103-ET-PG1101-2 | HTC-14 / CB-14 | 29103-PG-1101 | 29103-65R-ET-PG1101-02-01 | 13.1 | 29103-ET-PG1101-2-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/11.8M/525/120/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1201-1-1 | 29103-ET-PG1201-1 | HTC-12 / CB-12 | 29103-PG-1201, 29103-PE-1202, 29103-P-1200 | 29103-65R-ET-PG1201-01-01 | 13.1 | 29103-ET-PG1201-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/93.1M/2914/277/1.2M/LS23A/X/N12 | 93.1 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1201-2-1 | 29103-ET-PG1201-2 | HTC-08 / CB-08 | 29103-PG-1201 | 29103-65R-ET-PG1201-02-01 | 13.1 | 29103-ET-PG1201-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/8.6M/401/89.2/1.2M/LS23A/X/N12/XNF | 8.6 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1201-2-2 | 29103-ET-PG1201-2 | HTC-08 / CB-08 | 29103-PG-1201 | 29103-65R-ET-PG1201-02-01 | 13.1 | 29103-ET-PG1201-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/6.3M/294/65.4/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1201-2-3 | 29103-ET-PG1201-2 | HTC-08 / CB-08 | 29103-PG-1201 | 29103-65R-ET-PG1201-02-01 | 13.1 | 29103-ET-PG1201-2-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/11.8M/550/122/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1301-1-1 | 29103-ET-PG1301-1 | HTC-11 / CB-11 | 29103-PG-1301, 29103-PE-1302, 29103-P-1300 | 29103-65R-ET-PG1301-01-01 | 13.1 | 29103-ET-PG1301-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4734/89M/3035/277/1.2M/LS23A/X/N12 | 89 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1301-2-1 | 29103-ET-PG1301-2 | HTC-13 / CB-13 | 29103-PG-1301 | 29103-65R-ET-PG1301-02-01 | 13.1 | 29103-ET-PG1301-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/9.2M/409/93.3/1.2M/LS23A/X/N12/XNF | 9.2 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1301-2-2 | 29103-ET-PG1301-2 | HTC-13 / CB-13 | 29103-PG-1301 | 29103-65R-ET-PG1301-02-01 | 13.1 | 29103-ET-PG1301-2-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB3700/6.3M/280/63.9/1.2M/LS23A/X/N12/XMF | 6.3 m m | Levy Ostrup
EHT Trace | 29103-ET-PG1301-2-3 | 29103-ET-PG1301-2 | HTC-13 / CB-13 | 29103-PG-1301 | 29103-65R-ET-PG1301-02-01 | 13.1 | 29103-ET-PG1301-2-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3700/11.8M/525/120/1.2M/LS23A/X/N12/XMN | 11.8 m m | Levy Ostrup
EHT Trace | 29103-ET-SC1800-1-1 | 29103-ET-SC1800-1 | 29103-AMB-002 | 29103-ST-1815, 29103-ST-1814, 29103-ST-1813, 29103- ST-1812, 29103-SC-1803, 29103-SC-1800 | 29103-65R-ET-SC1800-01-01 | 13.1 | 29103-ET-SC1800-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB3914/39.4M/650/277/1.2M/LS23A/X/N12 | 39.4 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1001-1-1 | 29103-ET-ST1001-1 | 29103-AMB-002 | 29103-ST-1001 | 29103-65R-ET-ST1001-01-01 | 13.1 | 29103-ET-ST1001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/12.6M/169/89.3/1.2M/LS23A/X/N12/XNF | 12.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1001-1-2 | 29103-ET-ST1001-1 | 29103-AMB-002 | 29103-ST-1002, 29103-ST-1001 | 29103-65R-ET-ST1001-01-01 | 13.1 | 29103-ET-ST1001-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/26.5M/355/188/1.2M/LS23A/X/N12/XMN | 26.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1103-1-1 | 29103-ET-ST1103-1 | 29103-AMB-002 | 29103-ST-1104, 29103-ST-1103 | 29103-65R-ET-ST1103-01-01 | 13.1 | 29103-ET-ST1103-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.5M/282/136/1.2M/LS23A/X/N12/XNF | 17.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1103-1-2 | 29103-ET-ST1103-1 | 29103-AMB-002 | 29103-ST-1104 | 29103-65R-ET-ST1103-01-01 | 13.1 | 29103-ET-ST1103-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/293/141/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1103-1-3 | 29103-ET-ST1103-1 | 29103-AMB-002 | 29103-ST-1103 | 29103-65R-ET-ST1103-01-01 | 13.1 | 29103-ET-ST1103-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 55.2 Ω | 2026-05-18 | [12 empty] | E/32SA2170/9.5M/162/93/1.2M/LS23A/X/N12/XNF | 9.5 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1103-1-4 | 29103-ET-ST1103-1 | 29103-AMB-002 | 29103-ST-1103 | 29103-65R-ET-ST1103-01-01 | 13.1 | 29103-ET-ST1103-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 33.5 Ω | 2026-05-18 | [12 empty] | E/32SA2170/5.7M/97/55.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1103-1-5 | 29103-ET-ST1103-1 | 29103-AMB-002 | 29103-ST-1103 | 29103-65R-ET-ST1103-01-01 | 13.1 | 29103-ET-ST1103-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 75.6 Ω | 2026-05-18 | [12 empty] | D/32SA2170/13.1M/224/128/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1203-1-1 | 29103-ET-ST1203-1 | 29103-AMB-002 | 29103-ST-1204, 29103-ST-1203 | 29103-65R-ET-ST1203-01-01 | 13.1 | 29103-ET-ST1203-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | E/32SB2114/17.3M/282/135/1.2M/LS23A/X/N12/XNF | 17.3 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1203-1-2 | 29103-ET-ST1203-1 | 29103-AMB-002 | 29103-ST-1204 | 29103-65R-ET-ST1203-01-01 | 13.1 | 29103-ET-ST1203-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SB2114/18.2M/297/142/1.2M/LS23A/X/N12/XMN | 18.2 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1203-1-3 | 29103-ET-ST1203-1 | 29103-AMB-002 | 29103-ST-1203 | 29103-65R-ET-ST1203-01-01 | 13.1 | 29103-ET-ST1203-1-3.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 51.6 Ω | 2026-05-18 | [12 empty] | E/32SA2200/7.6M/127/79.7/1.2M/LS23A/X/N12/XNF | 7.6 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1203-1-4 | 29103-ET-ST1203-1 | 29103-AMB-002 | 29103-ST-1203 | 29103-65R-ET-ST1203-01-01 | 13.1 | 29103-ET-ST1203-1-4.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 38.6 Ω | 2026-05-18 | [12 empty] | E/32SA2200/5.7M/95/59.8/1.2M/LS23A/X/N12/XMF | 5.7 m m | Levy Ostrup
EHT Trace | 29103-ET-ST1203-1-5 | 29103-ET-ST1203-1 | 29103-AMB-002 | 29103-ST-1203 | 29103-65R-ET-ST1203-01-01 | 13.1 | 29103-ET-ST1203-1-5.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >550 MΩ | 88.7 Ω | 2026-05-18 | [12 empty] | D/32SA2200/13.1M/219/137/1.2M/LS23A/X/N12/XMN | 13.1 m m | Levy Ostrup
Power Cable | 29103-AMB-001 |  | 29103-HTP-002 HTC-03 | 29103-HTP-002 |  | 113 | 29103-AMB-001.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-002 |  | 29103-HTP-002 HTC-02 | 29103-HTP-002 |  | 113 | 29103-AMB-002.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-AMB-003 |  | 29103-HTP-002 HTC-01 | 29103-HTP-002 |  | 113 | 29103-AMB-003.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 8AWG | Levy Ostrup
Power Cable | 29103-ET-FG1101-1-PWK-1 | 29103-ET-FG1101-1 | 29103-AMB-001 | 29103-HTP-002 |  | 113 | 29103-ET-FG1101-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1103-1-PWK-1 | 29103-ET-FG1103-1 | 29103-AMB-001 | 29103-HTP-002 |  | 113 | 29103-ET-FG1103-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1105-1-PWK-1 | 29103-ET-FG1105-1 | 29103-AMB-002 | 29103-HTP-002 |  | 113 | 29103-ET-FG1105-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1201-1-PWK-1 | 29103-ET-FG1201-1 | 29103-AMB-001 | 29103-HTP-002 |  | 113 | 29103-ET-FG1201-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1203-1-PWK-1 | 29103-ET-FG1203-1 | 29103-AMB-001 | 29103-HTP-002 |  | 113 | 29103-ET-FG1203-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1301-1-PWK-1 | 29103-ET-FG1301-1 | 29103-AMB-003 | 29103-HTP-002 |  | 113 | 29103-ET-FG1301-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1303-1-PWK-1 | 29103-ET-FG1303-1 | 29103-AMB-003 | 29103-HTP-002 |  | 113 | 29103-ET-FG1303-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1401-1-PWK-1 | 29103-ET-FG1401-1 | 29103-AMB-003 | 29103-HTP-002 |  | 113 | 29103-ET-FG1401-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-FG1403-1-PWK-1 | 29103-ET-FG1403-1 | 29103-AMB-003 | 29103-HTP-002 |  | 113 | 29103-ET-FG1403-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1101-1-PWK-1 | 29103-ET-P1101-1 | 29103-HTP-002 HTC-37 | 29103-HTP-002 |  | 113 | 29103-ET-P1101-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | NO | [10 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 29 | Cable is pulled & glanded; no terms
Power Cable | 29103-ET-P1104-1-PWK-1 | 29103-ET-P1104-1 | 29103-HTP-002 HTC-35 | 29103-HTP-002 |  | 113 | 29103-ET-P1104-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 11 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 29
Power Cable | 29103-ET-P1104-2-PWK-1 | 29103-ET-P1104-2 | 29103-HTP-002 HTC-40 | 29103-HTP-002 |  | 113 | 29103-ET-P1104-2-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 10 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.5 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 29 | Missing cable tag both sides
Power Cable | 29103-ET-P1201-1-PWK-1 | 29103-ET-P1201-1 | 29103-HTP-002 HTC-39 | 29103-HTP-002 |  | 113 | 29103-ET-P1201-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 5 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 29 | Core markers missing; not termed
Power Cable | 29103-ET-P1204-1-PWK-1 | 29103-ET-P1204-1 | 29103-HTP-002 HTC-27 | 29103-HTP-002 |  | 113 | 29103-ET-P1204-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1204-2-PWK-1 | 29103-ET-P1204-2 | 29103-HTP-002 HTC-29 | 29103-HTP-002 |  | 113 | 29103-ET-P1204-2-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 28 | Missing cable tag; service loop on cold lead
Power Cable | 29103-ET-P1301-1-PWK-1 | 29103-ET-P1301-1 | 29103-HTP-002 HTC-38 | 29103-HTP-002 |  | 113 | 29103-ET-P1301-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1304-1-PWK-1 | 29103-ET-P1304-1 | 29103-HTP-002 HTC-09 | 29103-HTP-002 |  | 113 | 29103-ET-P1304-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1304-2-PWK-1 | 29103-ET-P1304-2 | 29103-HTP-002 HTC-19 | 29103-HTP-002 |  | 113 | 29103-ET-P1304-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1401-1-PWK-1 | 29103-ET-P1401-1 | 29103-HTP-002 HTC-05 | 29103-HTP-002 |  | 113 | 29103-ET-P1401-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1800-1-PWK-1 | 29103-ET-P1800-1 | 29103-HTP-002 HTC-26 | 29103-HTP-002 |  | 113 | 29103-ET-P1800-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-P1800-2-PWK-1 | 29103-ET-P1800-2 | 29103-HTP-002 HTC-16 | 29103-HTP-002 |  | 113 | 29103-ET-P1800-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1101-1-PWK-1 | 29103-ET-PE1101-1 | 29103-HTP-002 HTC-25 | 29103-HTP-002 |  | 113 | 29103-ET-PE1101-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 11 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 28
Power Cable | 29103-ET-PE1101-2-PWK-1 | 29103-ET-PE1101-2 | 29103-HTP-002 HTC-24 | 29103-HTP-002 |  | 113 | 29103-ET-PE1101-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1102-1-PWK-1 | 29103-ET-PE1102-1 | 29103-HTP-002 HTC-23 | 29103-HTP-002 |  | 113 | 29103-ET-PE1102-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 4 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 28/26 | No core markers / cable tags ¦ Not terminated ¦ No GRL on HT connector
Power Cable | 29103-ET-PE1201-1-PWK-1 | 29103-ET-PE1201-1 | 29103-HTP-002 HTC-22 | 29103-HTP-002 |  | 113 | 29103-ET-PE1201-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 28 | Cable tag upside down
Power Cable | 29103-ET-PE1201-2-PWK-1 | 29103-ET-PE1201-2 | 29103-HTP-002 HTC-20 | 29103-HTP-002 |  | 113 | 29103-ET-PE1201-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1202-1-PWK-1 | 29103-ET-PE1202-1 | 29103-HTP-002 HTC-18 | 29103-HTP-002 |  | 113 | 29103-ET-PE1202-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1301-1-PWK-1 | 29103-ET-PE1301-1 | 29103-HTP-002 HTC-10 | 29103-HTP-002 |  | 113 | 29103-ET-PE1301-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1301-2-PWK-1 | 29103-ET-PE1301-2 | 29103-HTP-002 HTC-07 | 29103-HTP-002 |  | 113 | 29103-ET-PE1301-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1302-1-PWK-1 | 29103-ET-PE1302-1 | 29103-HTP-002 HTC-06 | 29103-HTP-002 |  | 113 | 29103-ET-PE1302-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1401-1-PWK-1 | 29103-ET-PE1401-1 | 29103-HTP-002 HTC-04 | 29103-HTP-002 |  | 113 | 29103-ET-PE1401-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PE1802-1-PWK-1 | 29103-ET-PE1802-1 | 29103-HTP-002 HTC-17 | 29103-HTP-002 |  | 113 | 29103-ET-PE1802-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 8 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 28 | Needs core markers ¦ Cable tag upside down
Power Cable | 29103-ET-PE1803-1-PWK-1 | 29103-ET-PE1803-1 | 29103-HTP-002 HTC-21 | 29103-HTP-002 |  | 113 | 29103-ET-PE1803-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1101-1-PWK-1 | 29103-ET-PG1101-1 | 29103-HTP-002 HTC-15 | 29103-HTP-002 |  | 113 | 29103-ET-PG1101-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 10 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup | Sept 29 | Power cable missing core markers
Power Cable | 29103-ET-PG1101-2-PWK-1 | 29103-ET-PG1101-2 | 29103-HTP-002 HTC-14 | 29103-HTP-002 |  | 113 | 29103-ET-PG1101-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1201-1-PWK-1 | 29103-ET-PG1201-1 | 29103-HTP-002 HTC-12 | 29103-HTP-002 |  | 113 | 29103-ET-PG1201-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1201-2-PWK-1 | 29103-ET-PG1201-2 | 29103-HTP-002 HTC-08 | 29103-HTP-002 |  | 113 | 29103-ET-PG1201-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1301-1-PWK-1 | 29103-ET-PG1301-1 | 29103-HTP-002 HTC-11 | 29103-HTP-002 |  | 113 | 29103-ET-PG1301-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-PG1301-2-PWK-1 | 29103-ET-PG1301-2 | 29103-HTP-002 HTC-13 | 29103-HTP-002 |  | 113 | 29103-ET-PG1301-2-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-SC1800-1-PWK-1 | 29103-ET-SC1800-1 | 29103-AMB-002 | 29103-HTP-002 |  | 113 | 29103-ET-SC1800-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1001-1-PWK-1 | 29103-ET-ST1001-1 | 29103-AMB-002 | 29103-HTP-002 |  | 113 | 29103-ET-ST1001-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1103-1-PWK-1 | 29103-ET-ST1103-1 | 29103-AMB-002 | 29103-HTP-002 |  | 113 | 29103-ET-ST1103-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
Power Cable | 29103-ET-ST1203-1-PWK-1 | 29103-ET-ST1203-1 | 29103-AMB-002 | 29103-HTP-002 |  | 113 | 29103-ET-ST1203-1-PWK-1.pdf | YES | NO | N/A | N/A | N/A | NO | NO | N/A | N/A | NO | NO | [16 empty] | Teck | 10AWG | Levy Ostrup
RTD | 29103-ET-P1101-1-R-1 | 29103-ET-P1101-1 | 29103-HTP-002 (TB5 / CB-37) | PRODUCED EMULSION | 29103-ET-P1101-1 | 13.2 | 29103-ET-P1101-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | YES | YES | YES | YES | 9 | [11 empty] | Fluke 179 70180306 | 100 | 104 / 104 / 0.2 | 102 Ω / 102 Ω / 0.2 Ω |  |  | Levy Ostrup | Oct 1 2026 | - Switched term points with ETP11041R1
RTD | 29103-ET-P1104-1-R-1 | 29103-ET-P1104-1 | 29103-HTP-002 (TB5 / CB-35) | PRODUCED EMULSION | 29103-ET-P1104-1 | 13.2 | 29103-ET-P1104-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 7 | [11 empty] | Fluke 179 70180306 | 104.1 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30 2026 | - Switched termination points with ETP11011R1
RTD | 29103-ET-P1104-1-R-2 | 29103-ET-P1104-1 | 29103-HTP-002 (TB8 / I/O 2-3) | PRODUCED EMULSION | 29103-ET-P1104-1 | 13.2 | 29103-ET-P1104-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026
RTD | 29103-ET-P1104-2-R-1 | 29103-ET-P1104-2 | 29103-HTP-002 (TB5 / CB-40) | PRODUCED EMULSION | 29103-ET-P1104-2 | 13.2 | 29103-ET-P1104-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 8 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30 2026 | - RTD sitting on trace (MI)
RTD | 29103-ET-P1104-2-R-2 | 29103-ET-P1104-2 | 29103-HTP-002 (I/O 2-4 / TB-8) | PRODUCED EMULSION | 29103-ET-P1104-2 | 13.2 | 29103-ET-P1104-2-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 29 2026
RTD | 29103-ET-P1201-1-R-1 | 29103-ET-P1201-1 | 29103-HTP-002 HTC-39 | PRODUCED EMULSION | 29103-65R-ET-P1201-01-01 | 13.2 | 29103-ET-P1201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1204-1-R-1 | 29103-ET-P1204-1 | 29103-HTP-002 HTC-27 | PRODUCED EMULSION | 29103-65R-ET-P1204-01-01 | 13.2 | 29103-ET-P1204-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1204-1-R-2 | 29103-ET-P1204-1 | 29103-HTP-002 (TB8 / I/O 4-2) | PRODUCED EMULSION | 29103-ET-P1204-1 | 13.2 | 29103-ET-P1204-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026
RTD | 29103-ET-P1204-2-R-1 | 29103-ET-P1204-2 | 29103-HTP-002 (TB5 / HTC-29) | PRODUCED EMULSION | 29103-ET-P1204-2 | 13.2 | 29103-ET-P1204-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026
RTD | 29103-ET-P1204-2-R-2 | 29103-ET-P1204-2 | 29103-HTP-002 I/O-4-3 | PRODUCED EMULSION | 29103-65R-ET-P1204-02-01 | 13.2 | 29103-ET-P1204-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1301-1-R-1 | 29103-ET-P1301-1 | 29103-HTP-002 HTC-38 | PRODUCED EMULSION | 29103-65R-ET-P1301-01-01 | 13.2 | 29103-ET-P1301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1304-1-R-1 | 29103-ET-P1304-1 | 29103-HTP-002 HTC-09 | PRODUCED EMULSION | 29103-65R-ET-P1304-01-01 | 13.2 | 29103-ET-P1304-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1304-1-R-2 | 29103-ET-P1304-1 | 29103-HTP-002 I/O-1-3 | PRODUCED EMULSION | 29103-65R-ET-P1304-01-01 | 13.2 | 29103-ET-P1304-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1304-2-R-1 | 29103-ET-P1304-2 | 29103-HTP-002 HTC-19 | PRODUCED EMULSION | 29103-65R-ET-P1304-02-01 | 13.2 | 29103-ET-P1304-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1304-2-R-2 | 29103-ET-P1304-2 | 29103-HTP-002 I/O-3-3 | PRODUCED EMULSION | 29103-65R-ET-P1304-02-01 | 13.2 | 29103-ET-P1304-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1401-1-R-1 | 29103-ET-P1401-1 | 29103-HTP-002 HTC-05 | PRODUCED EMULSION | 29103-65R-ET-P1401-01-01 | 13.2 | 29103-ET-P1401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-P1800-1-R-1 | 29103-ET-P1800-1 | 29103-HTP-002 (TB-5 / CB-26) | PRODUCED EMULSION | 29103-ET-P1800-1 | 13.2 | 29103-ET-P1800-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | [12 empty] | Fluke 179 70180306 |  |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 29 2026
RTD | 29103-ET-P1800-2-R-1 | 29103-ET-P1800-2 | 29103-HTP-002 HTC-16 | PRODUCED EMULSION | 29103-65R-ET-P1800-02-01 | 13.2 | 29103-ET-P1800-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1101-1-R-1 | 29103-ET-PE1101-1 | 29103-HTP-002 (TB-5 / CB-25) | PRODUCED EMULSION | 29103-ET-PE1101-1 | 13.2 | 29103-ET-PE1101-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 |  |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 29 2026
RTD | 29103-ET-PE1101-2-R-1 | 29103-ET-PE1101-2 | 29103-HTP-002 (I/O 1-4 / TB-8) | PRODUCED EMULSION | 29103-ET-PE1101-2 | 13.2 | 29103-ET-PE1101-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30 2026
RTD | 29103-ET-PE1101-2-R-2 | 29103-ET-PE1101-2 | 29103-HTP-002 (I/O 1-4 / TB-8) | PRODUCED EMULSION | 29103-ET-PE1101-2 | 13.2 | 29103-ET-PE1101-2-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 Ω / 104 Ω / 0.2 Ω |  |  | Levy Ostrup | Sept 29 2026
RTD | 29103-ET-PE1102-1-R-1 | 29103-ET-PE1102-1 | 29103-HTP-002 (TB5 / CB-23) | PRODUCED EMULSION | 29103-ET-PE1102-1 | 13.2 | 29103-ET-PE1102-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 8 | [11 empty] | Fluke 179 70180306 | 100 |  | 102 Ω / 102 Ω / 102 Ω |  |  | Levy Ostrup | Sept 30 2026 | No stainless steel tags on the JB or the RTD, also not terminated and no core markers. ¦ No core markers for the RTD.
RTD | 29103-ET-PE1102-1-R-2 | 29103-ET-PE1102-1 | 29103-HTP-002 (TB5 / HTC-23) | PRODUCED EMULSION | 29103-ET-PE-1102-1 | 13.2 | 29103-ET-PE1102-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 Ω / 104 Ω / 0.2 Ω |  |  | Levy Ostrup | Sept 30, 2026 | No stainless steel tags on the JB or the RTD, also not terminated and no core markers. ¦ No core markers for the RTD.
RTD | 29103-ET-PE1201-1-R-1 | 29103-ET-PE1201-1 | 29103-HTP-002 | PRODUCED EMULSION | 29103-ET-PE1201-1 | 13.2 | 29103-ET-PE1201-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026
RTD | 29103-ET-PE1201-2-R-2 | 29103-ET-PE1201-2 | 29103-HTP-002 (TB8 / I/O 3-4) | PRODUCED EMULSION | 29103-ET-PE1201-2 | 13.2 | 29103-ET-PE1201-2-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026
RTD | 29103-ET-PE1202-1-R-1 | 29103-ET-PE1202-1 | 29103-HTP-002 (TB5 / HTC-18) | PRODUCED EMULSION | 29103-ET-PE1202-1 | 13.2 | 29103-ET-PE1202-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026 | Not terminated, no core markers for JB or the RTD. ¦ No stainless steel tags for the JB or RTD.
RTD | 29103-ET-PE1202-1-R-2 | 29103-ET-PE1202-1 | 29103-HTP-002 (TB8 / I/O 4-4) | PRODUCED EMULSION | 29103-ET-PE1202-1 | 13.2 | 29103-ET-PE1202-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 6 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026 | Not terminated, no core markers for JB or the RTD. ¦ No stainless steel tags for the JB or RTD.
RTD | 29103-ET-PE1301-1-R-1 | 29103-ET-PE1301-1 | 29103-HTP-002 HTC-10 | PRODUCED EMULSION | 29103-65R-ET-PE1301-01-01 | 13.2 | 29103-ET-PE1301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1301-2-R-2 | 29103-ET-PE1301-2 | 29103-HTP-002 I/O-2-1 | PRODUCED EMULSION | 29103-65R-ET-PE1301-02-01 | 13.2 | 29103-ET-PE1301-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1302-1-R-1 | 29103-ET-PE1302-1 | 29103-HTP-002 I/O-2-2 / CB-06 | PRODUCED EMULSION | 29103-4"-PE-1302-DAPCO-64H-ET Rev 1A2 Trace: 29103-ET-PE1302-1-1 | 13.2 | 29103-ET-PE1302-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 3 | [17 empty] | Levy Ostrup | 2026/08/12 | No stainless steel tags on JB or RTD, and wrong core markers.
RTD | 29103-ET-PE1302-1-R-2 | 29103-ET-PE1302-1 | 29103-HTP-002 I/O-2-2 / CB-06 | PRODUCED EMULSION | 29103-4"-PE-1302-DAPCO-64H-ET Rev 1A2 Trace: 29103-ET-PE1302-1-1 | 13.2 | 29103-ET-PE1302-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 3 | [17 empty] | Levy Ostrup | 2026/08/12 | No stainless steel tags on JB or RTD, and wrong core markers.
RTD | 29103-ET-PE1401-1-R-1 | 29103-ET-PE1401-1 | 29103-HTP-002 HTC-04 | PRODUCED EMULSION | 29103-65R-ET-PE1401-01-01 | 13.2 | 29103-ET-PE1401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PE1802-1-R-1 | 29103-ET-PE1802-1 | 29103-HTP-002 (TB-05 / CB-17) | PRODUCED EMULSION | 29103-ET-PE1802-1 | 13.2 | 29103-ET-PE1802-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026
RTD | 29103-ET-PE1803-1-R-1 | 29103-ET-PE1803-1 | 29103-HTP-002 (TB5 / HTC-21) | PRODUCED EMULSION | 29103-ET-PE1803-1 | 13.2 | 29103-ET-PE1803-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | NO | NO | 5 | [11 empty] | Fluke 179 70180306 |  |  | 104 / 104 / 0.2 |  |  | Levy Ostrup
RTD | 29103-ET-PE1803-1-R-2 | 29103-ET-PE1803-1 | 29103-HTP-002 (TB5 / HTC 21) | PRODUCED EMULSION | 29103-ET-PE1803-1 | 13.2 | 29103-ET-PE1803-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 Ω / 104 Ω / 0.2 Ω |  |  | Levy Ostrup | Sept 30 2026
RTD | 29103-ET-PG1101-1-R-1 | 29103-ET-PG1101-1 | 29103-HTP-002 (TB-5 / CB-15) | PRODUCED GAS | 29103-ET-PG1101-1 | 13.2 | 29103-ET-PG1101-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | NO | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  |  |  |  | Levy Ostrup | Sept 29 2026
RTD | 29103-ET-PG1101-1-R-2 | 29103-ET-PG1101-1 | 29103-HTP-002 (TB-5 / CB15) | PRODUCED GAS | 29103-ET-PG1101-1 | 13.2 | 29103-ET-PG1101-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 9 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 29 2026
RTD | 29103-ET-PG1101-2-R-1 | 29103-ET-PG1101-2 | 29103-HTP-002 (TB-5 / CB-14) | PRODUCED GAS | 29103-ET-PG1101-2 | 13.2 | 29103-ET-PG1101-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | [12 empty] | Fluke 179 70180306 |  |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 29 2026
RTD | 29103-ET-PG1201-1-R-1 | 29103-ET-PG1201-1 | 29103-HTP-002 HTC-12 | PRODUCED GAS | 29103-65R-ET-PG1201-01-01 | 13.2 | 29103-ET-PG1201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1201-1-R-2 | 29103-ET-PG1201-1 | 29103-HTP-002 HTC-02 | PRODUCED GAS | 29103-65R-ET-PG1201-01-01 | 13.2 | 29103-ET-PG1201-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1201-2-R-1 | 29103-ET-PG1201-2 | 29103-HTP-002 | PRODUCED GAS | 29103-ET-PG1201-2 | 13.2 | 29103-ET-PG1201-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | N/A | NO | YES | YES | NO | 8 | [11 empty] | Fluke 179 70180306 | 100 |  | 104 / 104 / 0.2 |  |  | Levy Ostrup | Sept 30, 2026
RTD | 29103-ET-PG1301-1-R-1 | 29103-ET-PG1301-1 | 29103-HTP-002 HTC-11 | PRODUCED GAS | 29103-65R-ET-PG1301-01-01 | 13.2 | 29103-ET-PG1301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1301-1-R-2 | 29103-ET-PG1301-1 | 29103-HTP-002 I/O-3-1 | PRODUCED GAS | 29103-65R-ET-PG1301-01-01 | 13.2 | 29103-ET-PG1301-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD | 29103-ET-PG1301-2-R-1 | 29103-ET-PG1301-2 | 29103-HTP-002 HTC-13 | PRODUCED GAS | 29103-65R-ET-PG1301-02-01 | 13.2 | 29103-ET-PG1301-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | N/A | NO | NO | NO | NO | [18 empty] | Levy Ostrup
RTD Cable | 29103-ET-P1101-1-R-1 | 29103-ET-P1101-1 | 29103-HTP-002 HTC-37 | 29103-HTP-002 |  | 113 | 29103-ET-P1101-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.2 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30 2026 | - ETP11011R1 swapped termination points with ETP11041R1
RTD Cable | 29103-ET-P1104-1-R-1 | 29103-ET-P1104-1 | 29103-HTP-002 HTC-35 | 29103-HTP-002 |  | 113 | 29103-ET-P1104-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.2 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | - ETP11041R1 swapped terminations with ETP11011R1 inside panel
RTD Cable | 29103-ET-P1104-1-R-2 | 29103-ET-P1104-1 | 29103-HTP-002 I/O-2-3 | 29103-HTP-002 |  | 113 | 29103-ET-P1104-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.2 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30 2026 | Needs cable tags
RTD Cable | 29103-ET-P1104-2-R-1 | 29103-ET-P1104-2 | 29103-HTP-002 HTC-40 | 29103-HTP-002 |  | 113 | 29103-ET-P1104-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.0 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30 2026
RTD Cable | 29103-ET-P1104-2-R-2 | 29103-ET-P1104-2 | 29103-HTP-002 I/O-2-4 | 29103-HTP-002 |  | 113 | 29103-ET-P1104-2-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.1 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | Needs cable tags
RTD Cable | 29103-ET-P1201-1-R-1 | 29103-ET-P1201-1 | 29103-HTP-002 HTC-39 | 29103-HTP-002 |  | 113 | 29103-ET-P1201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1204-1-R-1 | 29103-ET-P1204-1 | 29103-HTP-002 HTC-27 | 29103-HTP-002 |  | 113 | 29103-ET-P1204-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1204-1-R-2 | 29103-ET-P1204-1 | 29103-HTP-002 I/O-4-2 | 29103-HTP-002 |  | 113 | 29103-ET-P1204-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [10 empty] | 0.9 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | Needs cable tags
RTD Cable | 29103-ET-P1204-2-R-1 | 29103-ET-P1204-2 | 29103-HTP-002 HTC-29 | 29103-HTP-002 |  | 113 | 29103-ET-P1204-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [10 empty] | 0.9 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | Needs cable tags
RTD Cable | 29103-ET-P1204-2-R-2 | 29103-ET-P1204-2 | 29103-HTP-002 I/O-4-3 | 29103-HTP-002 |  | 113 | 29103-ET-P1204-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1301-1-R-1 | 29103-ET-P1301-1 | 29103-HTP-002 HTC-38 | 29103-HTP-002 |  | 113 | 29103-ET-P1301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1304-1-R-1 | 29103-ET-P1304-1 | 29103-HTP-002 HTC-09 | 29103-HTP-002 |  | 113 | 29103-ET-P1304-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1304-1-R-2 | 29103-ET-P1304-1 | 29103-HTP-002 I/O-1-3 | 29103-HTP-002 |  | 113 | 29103-ET-P1304-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1304-2-R-1 | 29103-ET-P1304-2 | 29103-HTP-002 HTC-19 | 29103-HTP-002 |  | 113 | 29103-ET-P1304-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1304-2-R-2 | 29103-ET-P1304-2 | 29103-HTP-002 I/O-3-3 | 29103-HTP-002 |  | 113 | 29103-ET-P1304-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1401-1-R-1 | 29103-ET-P1401-1 | 29103-HTP-002 HTC-05 | 29103-HTP-002 |  | 113 | 29103-ET-P1401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-P1800-1-R-1 | 29103-ET-P1800-1 | 29103-HTP-002 HTC-26 | 29103-HTP-002 |  | 113 | 29103-ET-P1800-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.1 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026
RTD Cable | 29103-ET-P1800-2-R-1 | 29103-ET-P1800-2 | 29103-HTP-002 HTC-16 | 29103-HTP-002 |  | 113 | 29103-ET-P1800-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1101-1-R-1 | 29103-ET-PE1101-1 | 29103-HTP-002 HTC-25 | 29103-HTP-002 |  | 113 | 29103-ET-PE1101-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.1 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | Needs cable tags
RTD Cable | 29103-ET-PE1101-2-R-1 | 29103-ET-PE1101-2 | 29103-HTP-002 HTC-24 | 29103-HTP-002 |  | 113 | 29103-ET-PE1101-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 10 | [9 empty] | N/A / N/A / N/A | 1.0 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026
RTD Cable | 29103-ET-PE1101-2-R-2 | 29103-ET-PE1101-2 | 29103-HTP-002 I/O-1-4 | 29103-HTP-002 |  | 113 | 29103-ET-PE1101-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | YES | NO | [16 empty] | ACIC | 16 AWG | Levy Ostrup | Sept 29 2026 | - No cable pulled
RTD Cable | 29103-ET-PE1102-1-R-1 | 29103-ET-PE1102-1 | 29103-HTP-002 HTC-23 | 29103-HTP-002 |  | 113 | 29103-ET-PE1102-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.1 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 29 2026 | - No cable tag
RTD Cable | 29103-ET-PE1102-1-R-2 | 29103-ET-PE1102-1 | 29103-HTP-002 I/O-3-2 | 29103-HTP-002 |  | 113 | 29103-ET-PE1102-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.1 / 1.1 / 1.2 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 29 2026 | - No cable tag
RTD Cable | 29103-ET-PE1201-1-R-1 | 29103-ET-PE1201-1 | 29103-HTP-002 HTC-22 | 29103-HTP-002 |  | 113 | 29103-ET-PE1201-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [10 empty] | 0.8 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | Missing cable tags
RTD Cable | 29103-ET-PE1201-2-R-2 | 29103-ET-PE1201-2 | 29103-HTP-002 I/O-3-4 | 29103-HTP-002 |  | 113 | 29103-ET-PE1201-2-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [10 empty] | 1.2 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026
RTD Cable | 29103-ET-PE1202-1-R-1 | 29103-ET-PE1202-1 | 29103-HTP-002 HTC-18 | 29103-HTP-002 |  | 113 | 29103-ET-PE1202-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 10 | [10 empty] | 0.7 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30 2026
RTD Cable | 29103-ET-PE1202-1-R-2 | 29103-ET-PE1202-1 | 29103-HTP-002 I/O-4-4 | 29103-HTP-002 |  | 113 | 29103-ET-PE1202-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 6 | [10 empty] | 0.7 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | Not terminated, needs core markers, cable tags
RTD Cable | 29103-ET-PE1301-1-R-1 | 29103-ET-PE1301-1 | 29103-HTP-002 HTC-10 | 29103-HTP-002 |  | 113 | 29103-ET-PE1301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1301-2-R-2 | 29103-ET-PE1301-2 | 29103-HTP-002 I/O-2-1 | 29103-HTP-002 |  | 113 | 29103-ET-PE1301-2-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1302-1-R-1 | 29103-ET-PE1302-1 | 29103-HTP-002 HTC-06 | 29103-HTP-002 |  | 113 | 29103-ET-PE1302-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1302-1-R-2 | 29103-ET-PE1302-1 | 29103-HTP-002 I/O-2-2 | 29103-HTP-002 |  | 113 | 29103-ET-PE1302-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1401-1-R-1 | 29103-ET-PE1401-1 | 29103-HTP-002 HTC-04 | 29103-HTP-002 |  | 113 | 29103-ET-PE1401-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PE1802-1-R-1 | 29103-ET-PE1802-1 | 29103-HTP-002 HTC-17 | 29103-HTP-002 |  | 113 | 29103-ET-PE1802-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 8 | [9 empty] | N/A / N/A / N/A | 1.2 / 1.1 / 1.2 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 29 2026 | - Missing core markers; missing boot
RTD Cable | 29103-ET-PE1803-1-R-1 | 29103-ET-PE1803-1 | 29103-HTP-002 HTC-21 | 29103-HTP-002 |  | 113 | 29103-ET-PE1803-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 6 | [10 empty] | 0.7 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | Not terminated, missing cable tag / core markers
RTD Cable | 29103-ET-PE1803-1-R-2 | 29103-ET-PE1803-1 | 29103-HTP-002 I/O-4-1 | 29103-HTP-002 |  | 113 | 29103-ET-PE1803-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.1 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 29 2026 | - No cable tag
RTD Cable | 29103-ET-PG1101-1-R-1 | 29103-ET-PG1101-1 | 29103-HTP-002 HTC-15 | 29103-HTP-002 |  | 113 | 29103-ET-PG1101-1-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.0 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 29 2026 | - No terms, boot, shrink or core markers
RTD Cable | 29103-ET-PG1101-1-R-2 | 29103-ET-PG1101-1 | 29103-HTP-002 HTC-01 | 29103-HTP-002 |  | 113 | 29103-ET-PG1101-1-R-2.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.3 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 29 2026 | - No cable tag
RTD Cable | 29103-ET-PG1101-2-R-1 | 29103-ET-PG1101-2 | 29103-HTP-002 HTC-14 | 29103-HTP-002 |  | 113 | 29103-ET-PG1101-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [9 empty] | N/A / N/A / N/A | 1.2 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | No cable tag
RTD Cable | 29103-ET-PG1201-1-R-1 | 29103-ET-PG1201-1 | 29103-HTP-002 HTC-12 | 29103-HTP-002 |  | 113 | 29103-ET-PG1201-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1201-1-R-2 | 29103-ET-PG1201-1 | 29103-HTP-002 HTC-02 | 29103-HTP-002 |  | 113 | 29103-ET-PG1201-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1201-2-R-1 | 29103-ET-PG1201-2 | 29103-HTP-002 HTC-08 | 29103-HTP-002 |  | 113 | 29103-ET-PG1201-2-R-1.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 9 | [10 empty] | 0.8 / OL / OL | Fluke 1587 FC 72300003 |  |  |  | ACIC | 16 AWG | Levy Ostrup | Sept 30, 2026 | Missing cable tags
RTD Cable | 29103-ET-PG1301-1-R-1 | 29103-ET-PG1301-1 | 29103-HTP-002 HTC-11 | 29103-HTP-002 |  | 113 | 29103-ET-PG1301-1-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1301-1-R-2 | 29103-ET-PG1301-1 | 29103-HTP-002 I/O-3-1 | 29103-HTP-002 |  | 113 | 29103-ET-PG1301-1-R-2.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-ET-PG1301-2-R-1 | 29103-ET-PG1301-2 | 29103-HTP-002 HTC-13 | 29103-HTP-002 |  | 113 | 29103-ET-PG1301-2-R-1.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-002 |  | 29103-HTP-002 HTC-20 | 29103-HTP-002 |  | 113 | 29103-RJB-002.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup
RTD Cable | 29103-RJB-003 |  | 29103-HTP-002 HTC-07 | 29103-HTP-002 |  | 113 | 29103-RJB-003.pdf | YES | NO | N/A | N/A | N/A | N/A | NO | N/A | N/A | NO | NO | [16 empty] | ACIC | 16AWG | Levy Ostrup

## 29151-HTP-001
29151-HTP-001
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29151-ET-DR4100-1-1 | 29151-ET-DR4100-1 |  | 29151-DR-4100 | 29151-65R-ET-DR4100-01-01 | 13.1 | 29151-ET-DR4100-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20XTVR1-CT | 7.3 m m | Levy Ostrup
EHT Trace | 29151-ET-FG4102-1-1 | 29151-ET-FG4102-1 |  | 29151-FG-4102, 29151-FG-4101, 29151-FG-4100 | 29151-65R-ET-FG4102-01-01 | 13.1 | 29151-ET-FG4102-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV1-CT | 11.4 m m | Levy Ostrup
EHT Trace | 29151-ET-FG4102-1-2 | 29151-ET-FG4102-1 |  | 29151-FG-4103, 29151-FG-4102 | 29151-65R-ET-FG4102-01-01 | 13.1 | 29151-ET-FG4102-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV1-CT | 8.7 m m | Levy Ostrup
EHT Trace | 29151-ET-HC4102-1-1 | 29151-ET-HC4102-1 |  | 29151-HC-4102 | 29151-65R-ET-HC4102-01-01 | 13.1 | 29151-ET-HC4102-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV1-CT | 39.9 m m | Levy Ostrup
EHT Trace | 29151-ET-MT0001-1-1 | 29151-ET-MT0001-1 |  | 29151-MT-0001 | 29151-65R-ET-MT0001-01-01 | 13.1 | 29151-ET-MT0001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR1-CT | 2.6 m m | Levy Ostrup
EHT Trace | 29151-ET-MT0002-1-1 | 29151-ET-MT0002-1 |  | 29151-MT-0002 | 29151-65R-ET-MT0002-01-01 | 13.1 | 29151-ET-MT0002-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 12HTV1-CT | 3.6 m m | Levy Ostrup
EHT Trace | 29151-ET-MT0002-1-2 | 29151-ET-MT0002-1 |  | 29151-MT-0002 | 29151-65R-ET-MT0002-01-01 | 13.1 | 29151-ET-MT0002-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 12HTV1-CT | 10.4 m m | Levy Ostrup
EHT Trace | 29151-ET-PG4100-1-1 | 29151-ET-PG4100-1 |  | 29151-PG-4101, 29151-PG-4100 | 29151-65R-ET-PG4100-01-01 | 13.1 | 29151-ET-PG4100-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV1-CT | 33.9 m m | Levy Ostrup
EHT Trace | 29151-ET-SC4102-1-1 | 29151-ET-SC4102-1 |  | 29151-SC-4103, 29151-SC-4102, 29151-DR-4104 | 29151-65R-ET-SC4102-01-01 | 13.1 | 29151-ET-SC4102-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/49.6M/868/120/1.2M/LS23A/X/N12 | 49.6 m m | Levy Ostrup
EHT Trace | 29151-ET-SC4102-1-2 | 29151-ET-SC4102-1 |  | 29203-ST-5005, 29151-ST-4101, 29151-ST-4100, 29151- SC-4102 | 29151-65R-ET-SC4102-01-01 | 13.1 | 29151-ET-SC4102-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SP4583/49.4M/1418/120/1.2M/LS23A/X/N12 | 49.4 m m | Levy Ostrup
EHT Trace | 29203-ET-DR5000-1-1 | 29203-ET-DR5000-1 |  | 29203-DR-5000 | 29203-65R-ET-DR5000-01-01 | 13.1 | 29203-ET-DR5000-1-1.pdf | YES | NO | YES | NO | NO | N/A | N/A | N/A | N/A | NO | NO |  | >2.2 GΩ | 10.2 Ω | 2026-05-17 | [12 empty] | D/32SQ3100/29.4M/1382/120/1.2M/LS23A/X/N12 | 29.4 m m | Levy Ostrup
EHT Trace | 29203-ET-HC5008-1-1 | 29203-ET-HC5008-1 |  | 29203-HC-5008, 29203-HC-5006, 29203-HC-5005 | 29203-65R-ET-HC5008-01-01 | 13.1 | 29203-ET-HC5008-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10HTV1-CT | 45.7 m m | Levy Ostrup
EHT Trace | 29203-ET-HC5008-1-2 | 29203-ET-HC5008-1 |  | 29203-HC-5008, 29203-HC-5007 | 29203-65R-ET-HC5008-01-01 | 13.1 | 29203-ET-HC5008-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10HTV1-CT | 11 m m | Levy Ostrup
EHT Trace | 29203-ET-HC5008-1-3 | 29203-ET-HC5008-1 |  | 29203-HC-5008 | 29203-65R-ET-HC5008-01-01 | 13.1 | 29203-ET-HC5008-1-3.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10HTV1-CT | 9.6 m m | Levy Ostrup
EHT Trace | 29203-ET-LIT0210-1-1 | 29203-ET-LIT0210-1 |  | 29203-LIT-0210 | 29203-65R-ET-LIT0210-01-01 | 13.1 | 29203-ET-LIT0210-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV1-CT | 15.5 m m | Levy Ostrup
EHT Trace | 29203-ET-LIT0211-1-1 | 29203-ET-LIT0211-1 |  | 29203-LIT-0211 | 29203-65R-ET-LIT0211-01-01 | 13.1 | 29203-ET-LIT0211-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV1-CT | 25 m m | Levy Ostrup
EHT Trace | 29203-ET-PE5002-2-1 | 29203-ET-PE5002-2 |  | 29203-PE-5002 | 29203-65R-ET-PE5002-02-01 | 13.1 | 29203-ET-PE5002-2-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 15HTV1-CT | 37.3 m m | Levy Ostrup
EHT Trace | 29203-ET-ST5001-1-1 | 29203-ET-ST5001-1 |  | 29203-ST-5001 | 29203-65R-ET-ST5001-01-01 | 13.1 | 29203-ET-ST5001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/20.6M/443/120/2.1M/LS23A/X/N12 | 20.6 m m | Levy Ostrup
Power Cable | 29151-ET-DR4100-1-PWK-1 | 29151-ET-DR4100-1 |  | 29151-HTP-001 |  | 113 | 29151-ET-DR4100-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 8 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 26 | Cable needs support - fixed Sept 25 ¦ Heat trace should be 43W p/m, has 66W p/m installed
Power Cable | 29151-ET-FG4102-1-PWK-1 | 29151-ET-FG4102-1 |  | 29151-HTP-001 |  | 113 | 29151-ET-FG4102-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25 | Check ISO - checked termination Sept 26 2026 ¦ Needs grommet on tray
Power Cable | 29151-ET-HC4102-1-PWK-1 | 29151-ET-HC4102-1 |  | 29151-HTP-001 |  | 113 | 29151-ET-HC4102-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 8 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 26 | No GRL
Power Cable | 29151-ET-MT0002-1-PWK-1 | 29151-ET-MT0002-1 |  | 29151-HTP-001 |  | 113 | 29151-ET-MT0002-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25, 2026 | Power kit underneath vessel needs tray support ¦ No GRL on PWK3
Power Cable | 29151-ET-PG4100-1-PWK-1 | 29151-ET-PG4100-1 |  | 29151-HTP-001 |  | 113 | 29151-ET-PG4100-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 8 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 26 | No GRL
Power Cable | 29151-ET-SC4102-1-PWK-1 | 29151-ET-SC4102-1 |  | 29151-HTP-001 |  | 113 | 29151-ET-SC4102-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 8 AWG | Levy Ostrup | Sept 25 2026 | Power kit installed but no cable pulled - Completed Sept 26
Power Cable | 29203-ET-DR5000-1-PWK-1 | 29203-ET-DR5000-1 |  | 29151-HTP-001 |  | 113 | 29203-ET-DR5000-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 8 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 24, 2026 | Missing core marker on white conductor - Fixed Sept 26
Power Cable | 29203-ET-HC5008-1-PWK-1 | 29203-ET-HC5008-1 |  | 29151-HTP-001 |  | 113 | 29203-ET-HC5008-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 6 AWG | Levy Ostrup | Sept 25, 2026 | Print calls for #6 AWG, #10 AWG is installed
Power Cable | 29203-ET-LIT0210-1-PWK-1 | 29203-ET-LIT0210-1 |  | 29151-HTP-001 |  | 113 | 29203-ET-LIT0210-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25 2026
Power Cable | 29203-ET-LIT0211-1-PWK-1 | 29203-ET-LIT0211-1 |  | 29151-HTP-001 |  | 113 | 29203-ET-LIT0211-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.5 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25, 2026
Power Cable | 29203-ET-PE5002-2-PWK-1 | 29203-ET-PE5002-2 |  | 29151-HTP-001 |  | 113 | 29203-ET-PE5002-2-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25 2026 | Location of RTD needs to be redlined in ISO.
Power Cable | 29203-ET-ST5001-1-PWK-1 | 29203-ET-ST5001-1 |  | 29151-HTP-001 |  | 113 | 29203-ET-ST5001-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.5 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25 2026
Power Cable | TANK1-1-PWK-1 | TANK1-1 |  | 29151-HTP-001 |  | 113 | TANK1-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 7 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 24, 2026 | Missing core marker on white conductor - Fixed Sept 26 ¦ Tray needs grommet
Power Cable | TANK1-2-PWK-1 | TANK1-2 |  | 29151-HTP-001 |  | 113 | TANK1-2-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 10 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25 2026
Power Cable | TANK1-3-PWK-1 | TANK1-3 |  | 29151-HTP-001 |  | 113 | TANK1-3-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 10 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25 2026
Power Cable | TANK1-4-PWK-1 | TANK1-4 |  | 29151-HTP-001 |  | 113 | TANK1-4-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 24 2026
Power Cable | TANK1-5-PWK-1 | TANK1-5 |  | 29151-HTP-001 |  | 113 | TANK1-5-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | YES | YES | 8 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup | Sept 25 | No parts, needs term kit

## 29152-HTP-001
29152-HTP-001
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
EHT Trace | 29152-ET-DR4200-1-1 | 29152-ET-DR4200-1 |  | 29152-DR-4200 | 29152-65R-ET-DR4200-01-01 | 13.1 | 29152-ET-DR4200-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20XTVR1-CT | 7.2 m m | Levy Ostrup
EHT Trace | 29152-ET-FG4202-1-1 | 29152-ET-FG4202-1 |  | 29152-FG-4202, 29152-FG-4201 | 29152-65R-ET-FG4202-01-01 | 13.1 | 29152-ET-FG4202-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV1-CT | 8.9 m m | Levy Ostrup
EHT Trace | 29152-ET-FG4202-1-2 | 29152-ET-FG4202-1 |  | 29152-FG-4203 | 29152-65R-ET-FG4202-01-01 | 13.1 | 29152-ET-FG4202-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV1-CT | 8.7 m m | Levy Ostrup
EHT Trace | 29152-ET-HC4202-1-1 | 29152-ET-HC4202-1 |  | 29152-HC-4202 | 29152-65R-ET-HC4202-01-01 | 13.1 | 29152-ET-HC4202-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV1-CT | 39.2 m m | Levy Ostrup
EHT Trace | 29152-ET-MT0001-1-1 | 29152-ET-MT0001-1 |  | 29152-MT-0001 | 29152-65R-ET-MT0001-01-01 | 13.1 | 29152-ET-MT0001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5XTVR1-CT | 2.6 m m | Levy Ostrup
EHT Trace | 29152-ET-MT0002-1-1 | 29152-ET-MT0002-1 |  | 29152-MT-0002 | 29152-65R-ET-MT0002-01-01 | 13.1 | 29152-ET-MT0002-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 12HTV1-CT | 3.6 m m | Levy Ostrup
EHT Trace | 29152-ET-MT0002-1-2 | 29152-ET-MT0002-1 |  | 29152-MT-0002 | 29152-65R-ET-MT0002-01-01 | 13.1 | 29152-ET-MT0002-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 12HTV1-CT | 10.4 m m | Levy Ostrup
EHT Trace | 29152-ET-PG4200-1-1 | 29152-ET-PG4200-1 |  | 29152-PG-4201, 29152-PG-4200 | 29152-65R-ET-PG4200-01-01 | 13.1 | 29152-ET-PG4200-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 5HTV1-CT | 34.3 m m | Levy Ostrup
EHT Trace | 29152-ET-SC4202-1-1 | 29152-ET-SC4202-1 |  | 29152-SC-4203, 29152-SC-4202, 29152-DR-4204 | 29152-65R-ET-SC4202-01-01 | 13.1 | 29152-ET-SC4202-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/44.8M/959/120/1.2M/LS23A/X/N12 | 44.8 m m | Levy Ostrup
EHT Trace | 29152-ET-SC4202-1-2 | 29152-ET-SC4202-1 |  | 29203-ST-5004, 29152-ST-4201, 29152-ST-4200, 29152- SC-4202 | 29152-65R-ET-SC4202-01-01 | 13.1 | 29152-ET-SC4202-1-2.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3100/51.5M/839/120/1.2M/LS23A/X/N12 | 51.5 m m | Levy Ostrup
EHT Trace | 29203-ET-DR5001-1-1 | 29203-ET-DR5001-1 |  | 29203-DR-5001 | 29203-65R-ET-DR5001-01-01 | 13.1 | 29203-ET-DR5001-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 20XTVR1-CT | 28 m m | Levy Ostrup
EHT Trace | 29203-ET-HC5012-1-1 | 29203-ET-HC5012-1 |  | 29203-HC-5012, 29203-HC-5011, 29203-HC-5010, 29203- HC-5009 | 29203-65R-ET-HC5012-01-01 | 13.1 | 29203-ET-HC5012-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 10HTV1-CT | 64 m m | Levy Ostrup
EHT Trace | 29203-ET-LIT0220-1-1 | 29203-ET-LIT0220-1 |  | 29203-LIT-0220 | 29203-65R-ET-LIT0220-01-01 | 13.1 | 29203-ET-LIT0220-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV1-CT | 14.7 m m | Levy Ostrup
EHT Trace | 29203-ET-LIT0221-1-1 | 29203-ET-LIT0221-1 |  | 29203-LIT-0221 | 29203-65R-ET-LIT0221-01-01 | 13.1 | 29203-ET-LIT0221-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 8HTV1-CT | 24.1 m m | Levy Ostrup
EHT Trace | 29203-ET-PE5002-1-1 | 29203-ET-PE5002-1 |  | 29203-PE-5002 | 29203-65R-ET-PE5002-01-01 | 13.1 | 29203-ET-PE5002-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | 15HTV1-CT | 37.3 m m | Levy Ostrup
EHT Trace | 29203-ET-ST5000-1-1 | 29203-ET-ST5000-1 |  | 29203-ST-5000 | 29203-65R-ET-ST5000-01-01 | 13.1 | 29203-ET-ST5000-1-1.pdf | YES | NO | NO | NO | NO | N/A | N/A | N/A | N/A | NO | NO | [16 empty] | D/32SQ3472/20.6M/443/120/2.1M/LS23A/X/N12 | 20.6 m m | Levy Ostrup
Power Cable | 29152-ET-DR4200-1-PWK-1 | 29152-ET-DR4200-1 |  | 29152-HTP-001 |  | 113 | 29152-ET-DR4200-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup |  | Incorrect HT installed, needs 43 W/m not 66 W/m
Power Cable | 29152-ET-FG4202-1-PWK-1 | 29152-ET-FG4202-1 |  | 29152-HTP-001 |  | 113 | 29152-ET-FG4202-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 8 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup |  | GRL missing
Power Cable | 29152-ET-HC4202-1-PWK-1 | 29152-ET-HC4202-1 |  | 29152-HTP-001 |  | 113 | 29152-ET-HC4202-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup |  | Doesn't have cable - fixed Sept 27
Power Cable | 29152-ET-MT0002-1-PWK-1 | 29152-ET-MT0002-1 |  | 29152-HTP-001 |  | 113 | 29152-ET-MT0002-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 8 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup |  | Missing cable supports @ gland - fixed Sept 27
Power Cable | 29152-ET-PG4200-1-PWK-1 | 29152-ET-PG4200-1 |  | 29152-HTP-001 |  | 113 | 29152-ET-PG4200-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 8 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup |  | Cable needs support at device gland - fixed Sept 27
Power Cable | 29152-ET-SC4202-1-PWK-1 | 29152-ET-SC4202-1 |  | 29152-HTP-001 |  | 113 | 29152-ET-SC4202-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup |  | Cable needs support ¦ Prints call for #8, #10 currently installed
Power Cable | 29203-ET-DR5001-1-PWK-1 | 29203-ET-DR5001-1 |  | 29152-HTP-001 |  | 113 | 29203-ET-DR5001-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup
Power Cable | 29203-ET-HC5012-1-PWK-1 | 29203-ET-HC5012-1 |  | 29152-HTP-001 |  | 113 | 29203-ET-HC5012-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 8 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 8 AWG | Levy Ostrup |  | Missing core markers
Power Cable | 29203-ET-LIT0220-1-PWK-1 | 29203-ET-LIT0220-1 |  | 29152-HTP-001 |  | 113 | 29203-ET-LIT0220-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 8 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup |  | Cable needs support at device gland
Power Cable | 29203-ET-LIT0221-1-PWK-1 | 29203-ET-LIT0221-1 |  | 29152-HTP-001 |  | 113 | 29203-ET-LIT0221-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup
Power Cable | 29203-ET-PE5002-1-PWK-1 | 29203-ET-PE5002-1 |  | 29152-HTP-001 |  | 113 | 29203-ET-PE5002-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup
Power Cable | 29203-ET-ST5000-1-PWK-1 | 29203-ET-ST5000-1 |  | 29152-HTP-001 |  | 113 | 29203-ET-ST5000-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.4 Ω / OL / OL | Fluke 1587 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup
Power Cable | TANK2-1-PWK-1 | TANK2-1 |  | 29152-HTP-001 |  | 113 | TANK2-1-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.2 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup
Power Cable | TANK2-2-PWK-1 | TANK2-2 |  | 29152-HTP-001 |  | 113 | TANK2-2-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 10 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup
Power Cable | TANK2-3-PWK-1 | TANK2-3 |  | 29152-HTP-001 |  | 113 | TANK2-3-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.2 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup
Power Cable | TANK2-4-PWK-1 | TANK2-4 |  | 29152-HTP-001 |  | 113 | TANK2-4-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | 550 MΩ / 550 MΩ / 550 MΩ | 0.2 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | Teck | 10 AWG | Levy Ostrup
Power Cable | TANK2-5-PWK-1 | TANK2-5 |  | 29152-HTP-001 |  | 113 | TANK2-5-PWK-1.pdf | YES | YES | N/A | N/A | N/A | YES | YES | N/A | N/A | NO | NO | 9 | [9 empty] | >550 MΩ / >550 MΩ / >550 MΩ | 0.3 Ω / OL / OL | Fluke 1587 FC 72300003 |  |  |  | TECK | 10 AWG | Levy Ostrup

## Drain Tank Fieldbus
Drain Tank Fieldbus
[8 empty] | CHECKSHEETS | [10 empty] | TEST RESULTS
Type | Tag | Circuit | Controller | System | ISO / Dwg | Form | File | ITR | Visual | Rec. Megger | Pre-Insul Megger | Post-Insul Megger | Cable IR | Cable Cont. | RTD Pre | RTD Post | Dated | Complete | Visual Initials | Rec. IR | Rec. Cont. | Rec. Date | Pre IR | Pre Cont. | Pre Date | Post IR | Post Cont. | Post Date | Cable IR | Cable Cont. | Meter | RTD Ω | RTD Pre (S/C/Com) | RTD Post (S/C/Com) | Part # / Cable | Length / Size | Inspected By | Date | Remarks
Fieldbus Cable | 29152-LIT-0203 |  |  |  |  | 113 | 29152-LIT-0203.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | 3.1 Ω / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | Sept 12/26 | - Pigtail on bend - No cable tags ¦ - Coil drain under boot - Loose instrument; needs to be tightened ¦ - Install grommet on FRT - All FRT up-top needs to be bonded to system
Fieldbus Cable | 29152-LIT-0205 |  |  |  |  | 113 | 29152-LIT-0205.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | 1.3 Ω / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | 9-11-2024 | - Orange lead is squished and bare wire is seen - re-term ¦ - Coil drain under boot; replace orange core marker
Fieldbus Cable | 29152-PIT-0205 |  |  |  |  | 113 | 29152-PIT-0205.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | 1.1 Ω / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | 9-11-2026 | - No cable tag; wrap cable into tray w/ 6' serv. loop. ¦ - Rubber grommet protruding through connector ¦ - Field run tray needs better support with strut (wobbles)
Fieldbus Cable | 29152-PY-0205 |  |  |  |  | 113 | 29152-PY-0205.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | 1 Ω / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | 9-11-2026 | Standard is to shrink and coil drain under boot.
Fieldbus Cable | 29152-XY-0201 |  |  |  |  | 113 | 29152-XY-0201.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | 1 Ω / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | 9-11-2026 | - Coil drain under boot ¦ - No cable tags.
Fieldbus Cable | 29152-XY-0202 |  |  |  |  | 113 | 29152-XY-0202.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | .9 Ω / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | 9-11-2026 | Drain should be coiled under boot.
Fieldbus Cable | 29152-XY-0203 |  |  |  |  | 113 | 29152-XY-0203.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | 1.0 / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | 9-11-26 | Service loop no bigger than 6'; No cable tags
Fieldbus Cable | 29152-XY-0204 |  |  |  |  | 113 | 29152-XY-0204.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | 1.1 / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | Sept 11/26 | - No cable tags ¦ - Drain should be coiled under boot.
Fieldbus Cable | 29203-XY-0220 |  |  |  |  | 113 | 29203-XY-0220.pdf | YES | YES | N/A | N/A | N/A | N/A | YES | N/A | N/A | YES | YES | 11 | [9 empty] | N/A / N/A / N/A | 1 Ω / OL / OL | Fluke 117 70201851MV |  |  |  | Fieldbus Type A | 18 AWG | Levy Ostrup | 9-11-2026 | - Drain should be coiled under the boot ¦ - No cable tags.