## Dashboard
K1B Well Pad – Equipment Inspection Tracker
Transmitter Inspection & Test Records + Pneumatically Actuated Valve Check Records
GO TO:
TRANSMITTERS LOGGED |  | VALVES LOGGED |  | MARKED READY (Y) | TOTAL EQUIPMENT
SYSTEM BREAKDOWN
100 Series
System | Transmitters | Valves | Total
STEAM
NATURAL GAS
PRODUCED EMULSION
200 Series
System | Transmitters | Valves | Total
STEAM
NATURAL GAS
PRODUCED EMULSION
Serial # Missing
QUICK TIPS
• Enter data in the Log tabs (grouped by section, dropdown columns are restricted to valid choices).
• Set column A ("Export to PDF (Y/N)") to Y on rows you want turned into filled PDFs.
• Use the Index tabs for a condensed view - click a row number to jump straight to it in the full log.
• Run the matching export script (export_to_pdf.py or export_valve_to_pdf.py) to generate PDFs.
• See the Instructions tab for full details, including the PDF export command-line options.

## Lists (hidden)
Y | Yes | Pass | ESDV | Inch | I | 150 | Flanged | 4-20 mA / HART | IESL | Sliding Stem | Valve Fails Open | mA
N | No | Fail | FCV | Metric | II | 300 | Threaded | Fieldbus | Other | Rotary | Valve Fails Closed | %
|  | N/A | LCV |  | III | 600 |  | Wireless |  | Quarter Turn | Valve Fails Last
|  |  | PCV |  | IV | 900 |  | Modbus |  | Throttle
|  |  | Other |  | V | 1200 |  | Pneumatic |  | Snap Acting
[5 empty] | VI | 1500
2500

## Valve Log 100
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date
N | [5 empty] | 29103-25J-106-01 | 29103-16"-ST-1800-DASB0-90H | 29103-PV-1200 |  | PCV |  | N/A | 51 | CA6NM SS/Nitrided | A487 gr CA6NM HF | N/A | N/A | Inch | 3 | N/A | SVI3 | IV | 1500 | N/A | N/A | 12" | Flanged | N/A | N/A | 0C18929.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-106-01 | 29103-16"-ST-1800-DASB0-90H | 29103-PV-1200 |  | PCV |  | S-26-019797 | 51 | CA6NM SS/Nitrided | A487 gr CA6NM HF | N/A | 41000 | Inch | 3" | F005382540 | SVI3 | IV | 1500 | N/A | N/A | 12 | Flanged | N/A | N/A | 0C18929.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-111-01 | 29103-6"-ST-1102-BASB0-64H | 29103-FV-1011 |  | FCV |  | 1000383587 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383579 | P3E HT | Inch | 4" | F005340804 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-111-01 | 29103-3"-ST-1101-DASB0-64H | 29103-FV-1012 |  | FCV |  | 1000383583 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389735 | P25E HT | Inch | 3" | F005340807 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-121-01 | 29103-6"-ST-1202-DASB0-64H | 29103-FV-1021 |  | FCV |  | 1000383602 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383595 | P3E HT | Inch | 4" | F005340829 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-121-01 | 29103-3"-ST-1201-DASB0-64H | 29103-FV-1022 |  | FCV |  | 1000383533 | PDA200 | 5CB TC | TC c/c S17400 carrier | 1000389751 | P25E HT | Inch | 3" | F005209238 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-131-01 | 29103-6"-ST-1302-DASB0-64H | 29103-FV-1031 |  | FCV |  | 1000383588 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383580 | P3E HT | Inch | 4" | F005340815 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-131-01 | 29103-3"-ST-1301-DASB0-64H | 29103-FV-1032 |  | FCV |  | 1000383564 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389736 | P25E HT | Inch | 3" | F005340816 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-141-01 | 29103-6"-ST-1402-DASB0-64H | 29103-FV-1041 |  | FCV |  | 1000383603 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383596 | P3E HT | Inch | 4" | F005340813 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-141-01 | 29103-3"-ST-1401-DASB0-64H | 29103-FV-1042 |  | FCV |  | 1000383534 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389752 | P25E HT | Inch | 3" | F005209236 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-151-01 | 29103-6"-ST-1502-DASB0-64H | 29103-FV-1051 |  | FCV |  | 1000383589 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383581 | P3E HT | Inch | 4" | F005340836 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-151-01 | 29103-3"-ST-1501-DASB0-64H | 29103-FV-1052 |  | FCV |  | 1000383565 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389737 | P25E HT | Inch | 3" | F005340809 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-161-01 | 29103-6"-ST-1602-DASB0-64H | 29103-FV-1061 |  | FCV |  | 1000383604 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383597 | P3E HT | Inch | 4" | F005340803 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-161-01 | 29103-3"-ST-1601-DASB0-64H | 29103-FV-1062 |  | FCV |  | 1000383535 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389753 | P25E HT | Inch | 3" | F005209241 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-171-01 | 29103-6"-ST-1702-DASB0-64H | 29103-FV-1071 |  | FCV |  | 1000383561 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383583 | P3E HT | Inch | 4" | F005340801 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-171-01 | 29103-3"-ST-1701-DASB0-64H | 29103-FV-1072 |  | FCV |  | 1000383566 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389738 | P25E HT | Inch | 3" | F005340818 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-111-01 | 29103-1"-FG-1105-DLHB0-38H-ET | 29103-FV-1015 |  | FCV |  | S-26-018955 | 88 Spring & Diaphragm | 316 SS | 316 SS | N/A | N/A | Inch | 0.8 | F005452608 | SVI3 SMART | IV | 1500 | N/A | N/A | 1 | Flanged | N/A | N/A | 0C18929.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-131-01 | 29103-1"-FG-1305-DLHB0-38H-ET | 29103-FV-1035 |  | FCV |  | N/A | 88 Spring & Diaphragm | 316 SS | 316 SS | N/A | N/A | Inch | 0.8 | N/A | SVI3 SMART | IV | 1500 | N/A | N/A | 1 | Flanged | N/A | N/A | 0C18929.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-151-01 | 29103-1"-FG-1505-DLHB0-38H-ET | 29103-FV-1055 |  | FCV |  | N/A | 88 Spring & Diaphragm | 316 SS | 316 SS | N/A | N/A | Inch | 0.8 | N/A | SVI3 SMART | IV | 1500 | N/A | N/A | 1 | Flanged | N/A | N/A | 0C18929.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-111-01 | 29103-1"-FG-1103-DLHB0-38H-ET | 29103-KV-1013 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224154 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-112-01 | 29103-1"-FG-1101-DLHB0-38H-ET | 29103-KV-1017 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224157 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-121-01 | 29103-1"-FG-1203-DLHB0-38H-ET | 29103-KV-1023 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224155 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-122-01 | 29103-1"-FG-1201-DLHB0-38H-ET | 29103-KV-1027 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224106 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-131-01 | 29103-1"-FG-1303-DLHB0-38H-ET | 29103-KV-1033 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224111 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-132-01 | 29103-1"-FG-1301-DLHB0-38H-ET | 29103-KV-1037 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224153 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-141-01 | 29103-1"-FG-1403-DLHB0-38H-ET | 29103-KV-1043 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224152 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-142-01 | 29103-1"-FG-1401-DLHB0-38H-ET | 29103-KV-1047 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224181 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-151-01 | 29103-1"-FG-1503-DLHB0-38H-ET | 29103-KV-1053 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224113 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-152-01 | 29103-1"-FG-1501-DLHB0-38H-ET | 29103-KV-1057 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224184 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-161-01 | 29103-1"-FG-1603-DLHB0-38H-ET | 29103-KV-1063 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224177 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-162-01 | 29103-1"-FG-1601-DLHB0-38H-ET | 29103-KV-1067 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224175 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-171-01 | 29103-1"-FG-1703-DLHB0-38H-ET | 29103-KV-1073 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224108 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-172-01 | 29103-1"-FG-1701-DLHB0-38H-ET | 29103-KV-1077 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224148 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-112-01 | 29103-4"-PE-1101-DAPC0-64H-ET | 29103-PV-1014 |  | PCV |  | 1000383571 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | 1000389743 | P25E | Inch | 1.5 | F005209232 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-122-01 | 29103-4"-PE-1201-DAPC0-64H-ET | 29103-PV-1024 |  | PCV |  | 1000383540 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005209243 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-132-01 | 29103-4"-PE-1301-DAPC0-64H-ET | 29103-PV-1034 |  | PCV |  | 1000383572 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005340817 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-142-01 | 29103-4"-PE-1401-DAPC0-64H-ET | 29103-PV-1044 |  | PCV |  | 1000383541 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005209347 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-152-01 | 29103-4"-PE-1501-DAPC0-64H-ET | 29103-PV-1054 |  | PCV |  | 1000383573 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005340832 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-162-01 | 29103-4"-PE-1601-DAPC0-64H-ET | 29103-PV-1064 |  | PCV |  | 1000383542 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005209242 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-172-01 | 29103-4"-PE-1701-DAPC0-64H-ET | 29103-PV-1074 |  | PCV |  | 1000383574 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005340799 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-112-01 | 29103-4"-PE-1102-DAPC0-64H-ET | 29103-XV-1011 |  |  |  | 3656446-011 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129208 | 4TF9RBPA105N |  |  | F005266343 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-112-01 | 29103-4"-PE-1103-DAPC0-64H-ET | 29103-XV-1012 |  |  |  | 3656446-017 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129209 | 4TF9RBPA105N |  |  | F005266334 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-122-01 | 29103-4"-PE-1202-DAPC0-64H-ET | 29103-XV-1021 |  |  |  | 3656446-024 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129210 | 4TF9RBPA105N |  |  | F005266348 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-122-01 | 29103-4"-PE-1203-DAPC0-64H-ET | 29103-XV-1022 |  |  |  | 3656446-003 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129211 | 4TF9RBPA105N |  |  | F005266332 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-132-01 | 29103-4"-PE-1302-DAPC0-64H-ET | 29103-XV-1031 |  |  |  | 3656446-020 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129212 | 4TF9RBPA105N |  |  | F005266353 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-132-01 | 29103-4"-PE-1303-DAPC0-64H-ET | 29103-XV-1032 |  |  |  | 3656446-023 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129213 | 4TF9RBPA105N |  |  | F005266335 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-142-01 | 29103-4"-PE-1402-DAPC0-64H-ET | 29103-XV-1041 |  |  |  | 3656446-018 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129214 | 4TF9RBPA105N |  |  | F005266350 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-142-01 | 29103-4"-PE-1403-DAPC0-64H-ET | 29103-XV-1042 |  |  |  | 3656446-028 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129215 | 4TF9RBPA105N |  |  | F005266333 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-152-01 | 29103-4"-PE-1502-DAPC0-64H-ET | 29103-XV-1051 |  |  |  | 3656446-027 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129216 | 4TF9RBPA105N |  |  | F005266347 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-152-01 | 29103-4"-PE-1503-DAPC0-64H-ET | 29103-XV-1052 |  |  |  | 3656446-021 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129217 | 4TF9RBPA105N |  |  | F005266329 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-162-01 | 29103-4"-PE-1602-DAPC0-64H-ET | 29103-XV-1061 |  |  |  | 3656446-025 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129218 | 4TF9RBPA105N |  |  | F005266349 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-162-01 | 29103-4"-PE-1603-DAPC0-64H-ET | 29103-XV-1062 |  |  |  | 3656446-022 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129219 | 4TF9RBPA105N |  |  | F005266338 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-172-01 | 29103-4"-PE-1702-DAPC0-64H-ET | 29103-XV-1071 |  |  |  | 3656446-008 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129220 | 4TF9RBPA105N |  |  | F005266331 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-172-01 | 29103-4"-PE-1703-DAPC0-64H-ET | 29103-XV-1072 |  |  |  | 3656446-007 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129221 | 4TF9RBPA105N |  |  | F005266325 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-106-01 | 29103-10"-PE-1802-DAPC0-64H-ET | 29103-XV-1520 |  |  |  | 3656469-001 | LPS-25A-485L-FC4-2 | F51+TCC | F316+TCC | YDFQ25129207 | 10TF9RBPA105N |  |  | F005266356 | DVC-6200 AD | V | 900

## Transmitter Log 100
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature
N |  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1014 | Pressure Transmitter | PRODUCED EMULSION | PAD A P01 PRODUCED EMULSION PRES | 29103-25J-112-01 | 29103-4"-PE-1101-DAPC0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884781 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 24.1 | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | [52 empty] | Pass | Example row - for reference only. Delete or overwrite before logging real data. | L. Olsen | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1011 | Vortex Flow Meter | STEAM | PAD A S01 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-112-01 | 29103-4"-ST-1100-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13949848 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.754 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1012 | Vortex Flow Meter | STEAM | PAD A S01 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-111-01 | 29103-3"-ST-1101-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13948492 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.614 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1021 | Vortex Flow Meter | STEAM | PAD A S02 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-121-01 | 29103-4"-ST-1200-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13939849 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.646 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-22
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1022 | Vortex Flow Meter | STEAM | PAD A S02 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-121-01 | 29103-3"-ST-1201-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13949011 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.491 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | N/A | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1031 | Vortex Flow Meter | STEAM | PAD A S03 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-131-01 | 29103-4"-ST-1300-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13949012 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.67 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1032 | Vortex Flow Meter | STEAM | PAD A S03 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-131-01 | 29103-3"-ST-1301-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13950338 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.429 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1041 | Vortex Flow Meter | STEAM | PAD A S04 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-141-01 | 29103-4"-ST-1400-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13950856 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.681 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1042 | Vortex Flow Meter | STEAM | PAD A S04 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-141-01 | 29103-3"-ST-1401-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13950339 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.484 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.3 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1051 | Vortex Flow Meter | STEAM | PAD A S05 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-151-01 | 29103-4"-ST-1500-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13950845 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.76 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1052 | Vortex Flow Meter | STEAM | PAD A S05 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-151-01 | 29103-3"-ST-1501-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13951880 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.388 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1061 | Vortex Flow Meter | STEAM | PAD A S06 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-161-01 | 29103-4"-ST-1600-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13951881 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.694 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1062 | Vortex Flow Meter | STEAM | PAD A S06 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-161-01 | 29103-3"-ST-1601-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13950340 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.661 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1071 | Vortex Flow Meter | STEAM | PAD A S07 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-171-01 | 29103-4"-ST-1700-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13950858 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1072 | Vortex Flow Meter | STEAM | PAD A S07 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-171-01 | 29103-3"-ST-1701-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13951882 | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | 10.743 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1200 | Pressure Transmitter | STEAM | PAD A HP STEAM TO WELL PAD | 29103-25J-106-01 | 29103-16"-ST-1802-DASB0-90H | ROSEMOUNT | 3051T | 26SIPG3884732 | 0 - 10000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1201 | Pressure Transmitter | STEAM | PAD A HP STEAM TO WELL PAD | 29103-25J-106-01 | 29103-16"-ST-1802-DASB0-90H | ROSEMOUNT | 3051T | 26SIPG3884728 | 0 - 10000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1202 | Pressure Transmitter | STEAM | PAD A HP STEAM FROM FLOWLINE | 29103-25J-106-01 | 29103-16"-ST-1802-DASB0-90H | ROSEMOUNT | 3051T | 26SIPG3884727 | 0 - 10000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1100 | Pressure Transmitter | STEAM | PAD A HP STEAM FROM FLOWLINE | 29103-25J-106-01 | 29103-16"-ST-1800-DASB0-90H | ROSEMOUNT | 3144P | 26SITC3660170 | -50 - 400ºC | -200 - 600ºC | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1011 | Pressure Transmitter | STEAM | PAD A S01 HP STM TO INJC WELL TOE | 29103-25J-111-01 | 29103-6"-ST-1102-DASB0-64H | ROSEMOUNT | 3051T | 26SIPG3884776 | 0 - 8000 kPa-g | -101 to 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1012 | Pressure Transmitter | STEAM | PAD A S01 HP STM TO INJC WELL HEEL | 29103-25J-111-01 | 29103-4"-ST-1103-DASB0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884782 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1021 | Pressure Transmitter | STEAM | PAD A S02 HP STM TO INJC WELL TOE | 29103-25J-121-01 | 29103-6"-ST-1202-DASB0-64H | ROSEMOUNT | 3051T | 26SIPG3884778 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1022 | Pressure Transmitter | STEAM | PAD A S02 HP STM TO INJC WELL HEEL | 29103-25J-121-01 | 29103-4"-ST-1203-DASB0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884777 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1031 | Pressure Transmitter | STEAM | PAD A S03 HP STM TO INJC WELL TOE | 29103-25J-131-01 | 29103-6"-ST-1302-DASB0-64H | ROSEMOUNT | 3051T | 26SIPG3885068 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1032 | Pressure Transmitter | STEAM | PAD A S03 HP STM TO INJC WELL HEEL | 29103-25J-131-01 | 29103-4"-ST-1303-DASB0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3885067 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1041 | Pressure Transmitter | STEAM | PAD A S04 HP STM TO INJC WELL TOE | 29103-25J-141-01 | 29103-6"-ST-1402-DASB0-64H | ROSEMOUNT | 3051T | 26SIPG3884596 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1042 | Pressure Transmitter | STEAM | PAD A S04 HP STM TO INJC WELL HEEL | 29103-25J-141-01 | 29103-6"-ST-1402-DASB0-64H | ROSEMOUNT | 3051T | 26SIPG3884595 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1051 | Pressure Transmitter | STEAM | PAD A S05 HP STM TO INJC WELL TOE | 29103-25J-151-01 | 29103-6"-ST-1502-DASB0-64H | ROSEMOUNT | 3051T | 26SIPG3884752 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1052 | Pressure Transmitter | STEAM | PAD A S05 HP STM TO INJC WELL HEEL | 29103-25J-151-01 | 29103-4"-ST-1503-DASB0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884595 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1061 | Pressure Transmitter | STEAM | PAD A S06 HP STM TO INJC WELL TOE | 29103-25J-161-01 | 29103-6"-ST-1602-DASB0-64H | ROSEMOUNT | 3051T | 26SIPG3884746 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1062 | Pressure Transmitter | STEAM | PAD A S06 HP STM TO INJC WELL HEEL | 29103-25J-161-01 | 29103-4"-ST-1603-DASB0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884742 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1071 | Pressure Transmitter | STEAM | PAD A S07 HP STM TO INJC WELL TOE | 29103-25J-171-01 | 29103-6"-ST-1702-DASB0-64H | ROSEMOUNT | 3051T | 26SIPG3884739 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1072 | Pressure Transmitter | STEAM | PAD A S07 HP STM TO INJC WELL HEEL | 29103-25J-171-01 | 29103-4"-ST-1703-DASB0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884736 | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1014 | Pressure Transmitter | PRODUCED EMULSION | PAD A P01 PRODUCED EMULSION PRESSURE | 29103-25J-112-01 | 29103-4"-PE-1101-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884781 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.6 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1018 | Pressure Transmitter | PRODUCED GAS | PAD A P01 PRODUCED VAPOR PRESSURE | 29103-25J-112-01 | 29103-4"-PG-1101-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884779 | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1014 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A P01 PRODUCED EMULSION HEAD | 29103-25J-112-01 | 29103-4"-PE-1101-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662822 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.2 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1024 | Pressure Transmitter | PRODUCED EMULSION | PAD A P02 PRODUCED EMULSION PRESSURE | 29103-25J-122-01 | 29103-4"-PE-1201-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884604 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1028 | Pressure Transmitter | PRODUCED GAS | PAD A P02 PRODUCED VAPOR PRESSURE | 29103-25J-122-01 | 29103-4"-PG-1201-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884602 | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1024 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A P02 PRODUCED EMULSION HEAD | 29103-25J-122-01 | 29103-4"-PE-1201-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662820 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1034 | Pressure Transmitter | PRODUCED EMULSION | PAD A P03 PRODUCED EMULSION PRESSURE | 29103-25J-132-01 | 29103-4"-PE-1301-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3885066 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1038 | Pressure Transmitter | PRODUCED GAS | PAD A P03 PRODUCED VAPOR PRESSURE | 29103-25J-132-01 | 29103-4"-PG-1301-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884597 | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1034 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A P03 PRODUCED EMULSION HEAD | 29103-25J-132-01 | 29103-4"-PE-1301-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662817 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1044 | Pressure Transmitter | PRODUCED EMULSION | PAD A P04 PRODUCED EMULSION PRESSURE | 29103-25J-142-01 | 29103-4"-PE-1401-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884594 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1048 | Pressure Transmitter | PRODUCED GAS | PAD A P04 PRODUCED VAPOR PRESSURE | 29103-25J-142-01 | 29103-4"-PG-1401-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884753 | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1044 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A P04 PRODUCED EMULSION HEAD | 29103-25J-142-01 | 29103-4"-PE-1401-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662816 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1054 | Pressure Transmitter | PRODUCED EMULSION | PAD A P05 PRODUCED EMULSION PRESSURE | 29103-25J-152-01 | 29103-4"-PE-1501-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884749 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1058 | Pressure Transmitter | PRODUCED GAS | PAD A P05 PRODUCED VAPOR PRESSURE | 29103-25J-152-01 | 29103-4"-PG-1501-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884747 | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1054 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A P05 PRODUCED EMULSION HEAD | 29103-25J-152-01 | 29103-4"-PE-1501-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662814 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1064 | Pressure Transmitter | PRODUCED EMULSION | PAD A P06 PRODUCED EMULSION PRESSURE | 29103-25J-162-01 | 29103-4"-PE-1601-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884731 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1068 | Pressure Transmitter | PRODUCED GAS | PAD A P06 PRODUCED VAPOR PRESSURE | 29103-25J-162-01 | 29103-4"-PG-1601-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884740 | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1064 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A P06 PRODUCED EMULSION HEAD | 29103-25J-162-01 | 29103-4"-PE-1601-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662812 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1074 | Pressure Transmitter | PRODUCED EMULSION | PAD A P07 PRODUCED EMULSION PRESSURE | 29103-25J-172-01 | 29103-4"-PE-1701-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884735 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1078 | Pressure Transmitter | PRODUCED GAS | PAD A P07 PRODUCED VAPOR PRESSURE | 29103-25J-172-01 | 29103-4"-PG-1701-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884733 | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1074 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A P07 PRODUCED EMULSION HEAD | 29103-25J-172-01 | 29103-4"-PE-1701-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662810 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.3 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1014 | Coriolis Flow Meter | PRODUCED EMULSION | PAD A P01 PRODUCED EMULSION FLOW | 29103-25J-111-01 | 29103-4"-PE-1101-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 | G250000007603631 | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1024 | Coriolis Flow Meter | PRODUCED EMULSION | PAD A P02 PRODUCED EMULSION FLOW | 29103-25J-121-01 | 29103-4"-PE-1201-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 | G250000007603632 | 0 to 30 m3/h @flow | 1.82 to 90.91 m3/h @flow | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1034 | Coriolis Flow Meter | PRODUCED EMULSION | PAD A P03 PRODUCED EMULSION FLOW | 29103-25J-131-01 | 29103-4"-PE-1301-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 | G250000007603633 | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1044 | Coriolis Flow Meter | PRODUCED EMULSION | PAD A P05 PRODUCED EMULSION FLOW | 29103-25J-141-01 | 29103-4"-PE-1501-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 | G250000007603634 | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1054 | Coriolis Flow Meter | PRODUCED EMULSION | PAD A P05 PRODUCED EMULSION FLOW | 29103-25J-151-01 | 29103-4"-PE-1601-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 | G250000007603635 | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1064 | Coriolis Flow Meter | PRODUCED EMULSION | PAD A P06 PRODUCED EMULSION FLOW | 29103-25J-161-01 | 29103-4"-PE-1601-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 | G250000007603675 | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1074 | Coriolis Flow Meter | PRODUCED EMULSION | PAD A P07 PRODUCED EMULSION FLOW | 29103-25J-171-01 | 29103-4"-PE-1701-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 | G250000007603676 | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | 10.492 | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1010A | Temperature Transmitter | PRODUCED EMULSION | PAD A P01 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-112-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768587 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1010J | Temperature Transmitter | PRODUCED EMULSION | PAD A P01 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-112-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768575 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1020A | Temperature Transmitter | PRODUCED EMULSION | PAD A P02 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-122-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768573 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1020J | Temperature Transmitter | PRODUCED EMULSION | PAD A P02 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-122-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768571 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1030A | Temperature Transmitter | PRODUCED EMULSION | PAD A P03 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-132-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768568 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1030J | Temperature Transmitter | PRODUCED EMULSION | PAD A P03 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-132-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768566 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1040A | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD A P04 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-142-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768564 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1040J | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD A P04 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-142-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768591 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1050A | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD A P05 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-152-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768589 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1050J | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD A P05 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-152-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3768570 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1060A | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD A P06 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-162-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3771273 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1060J | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD A P06 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-162-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3771271 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1070J | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD A P07 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-172-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | 26SITD3771265 | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1070A | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD A P07 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-172-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 | N/A | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1015 | Pressure Transmitter | PRODUCED EMULSION | PAD A S01 RETURN FLUID TO PROD WELL HEAD | 29103-25J-112-01 | 29103-4"-P-1101-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884780 | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1015 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A S01 RETURN FLUID TO PROD WELL HEADER | 29103-25J-112-01 | 29103-4"-P-1101-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662821 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.6 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1025 | Pressure Transmitter | PRODUCED EMULSION | PAD A S02 RETURN FLUID TO PROD WELL HEAD | 29103-25J-122-01 | 29103-4"-P-1201-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884603 | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1025 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A S02 RETURN FLUID TO PROD WELL HEADER | 29103-25J-122-01 | 29103-4"-P-1201-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662819 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1035 | Pressure Transmitter | PRODUCED EMULSION | PAD A S03 RETURN FLUID TO PROD WELL HEAD | 29103-25J-132-01 | 29103-4"-P-1301-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3885065 | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1035 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A S03 RETURN FLUID TO PROD WELL HEADER | 29103-25J-132-01 | 29103-4"-P-1301-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662818 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1045 | Pressure Transmitter | PRODUCED EMULSION | PAD A S04 RETURN FLUID TO PROD WELL HEAD | 29103-25J-142-01 | 29103-4"-P-1401-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884593 | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1045 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A S04 RETURN FLUID TO PROD WELL HEADER | 29103-25J-142-01 | 29103-4"-P-1401-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662815 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.6 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1055 | Pressure Transmitter | PRODUCED EMULSION | PAD A S05 RETURN FLUID TO PROD WELL HEAD | 29103-25J-152-01 | 29103-4"-P-1501-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884748 | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1055 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A S05 RETURN FLUID TO PROD WELL HEADER | 29103-25J-152-01 | 29103-4"-P-1501-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662813 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1065 | Pressure Transmitter | PRODUCED EMULSION | PAD A S06 RETURN FLUID TO PROD WELL HEAD | 29103-25J-162-01 | 29103-4"-P-1601-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884741 | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1065 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A S06 RETURN FLUID TO PROD WELL HEADER | 29103-25J-162-01 | 29103-4"-P-1601-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662811 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1075 | Pressure Transmitter | PRODUCED EMULSION | PAD A S07 RETURN FLUID TO PROD WELL HEAD | 29103-25J-172-01 | 29103-4"-P-1701-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 | 26SIPG3884734 | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1075 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD A S07 RETURN FLUID TO PROD WELL HEADER | 29103-25J-172-01 | 29103-4"-P-1701-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3662851 | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1015 | Vortex Flow Meter | NATURAL GAS | PAD A S01 NG TO INJC WELL TOE FLOW CTRL | 29103-25J-111-01 | 29103-1"-FG-1105-DLHB0-38H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13953601 | 0 to 30 m3/h @flow | 1.82 to 90.91 m3/h @flow | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1035 | Vortex Flow Meter | NATURAL GAS | PAD A S03 NG TO INJC WELL TOE FLOW CTRL | 29103-25J-131-01 | 29103-1"-FG-1305-DLHB0-38H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13957129 | 0 to 30 m3/h @flow | 1.82 to 90.91 m3/h @flow | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-1055 | Vortex Flow Meter | NATURAL GAS | PAD A S05 NG TO INJC WELL TOE FLOW CTRL | 29103-25J-151-01 | 29103-1"-FG-1505-DLHB0-38H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 | 13953602 | 0 to 30 m3/h @flow | 1.82 to 90.91 m3/h @flow | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1013 | Pressure Transmitter | NATURAL GAS | PAD A S01 NG INJECTION PRESSURE | 29103-25J-111-01 | 29103-1"-FG-1103-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884042 | 0 - 4000 kPa-g | -101 to 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1017 | Pressure Transmitter | NATURAL GAS | PAD A P01 NG INJC PRESSURE | 29103-25J-112-01 | 29103-1"-FG-1101-DLHB0-38H-ET | ROSEMOUNT | 3051T | N/A | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1023 | Pressure Transmitter | NATURAL GAS | PAD A S02 NG INJECTION PRESSURE | 29103-25J-121-01 | 29103-1"-FG-1203-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884003 | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1027 | Pressure Transmitter | NATURAL GAS | PAD A P02 NG INJC PRESSURE | 29103-25J-122-01 | 29103-1"-FG-1201-DLHB0-38H-ET | ROSEMOUNT | 3051T | N/A | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1033 | Pressure Transmitter | NATURAL GAS | PAD A S03 NG INJECTION PRESSURE | 29103-25J-131-01 | 29103-1"-FG-1303-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884957 | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1037 | Pressure Transmitter | NATURAL GAS | PAD A P03 NG INJC PRESSURE | 29103-25J-132-01 | 29103-1"-FG-1301-DLHB0-38H-ET | ROSEMOUNT | 3051T | N/A | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1043 | Pressure Transmitter | NATURAL GAS | PAD A S04 NG INJECTION PRESSURE | 29103-25J-141-01 | 29103-1"-FG-1403-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884458 | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1047 | Pressure Transmitter | NATURAL GAS | PAD A P04 NG INJC PRESSURE | 29103-25J-142-01 | 29103-1"-FG-1401-DLHB0-38H-ET | ROSEMOUNT | 3051T | N/A | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1057 | Pressure Transmitter | NATURAL GAS | PAD A P05 NG INJC PRESSURE | 29103-25J-152-01 | 29103-1"-FG-1501-DLHB0-38H-ET | ROSEMOUNT | 3051T | N/A | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1063 | Pressure Transmitter | NATURAL GAS | PAD A S06 NG INJECTION PRESSURE | 29103-25J-161-01 | 29103-1"-FG-1603-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884552 | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1067 | Pressure Transmitter | NATURAL GAS | PAD A P06 NG INJC PRESSURE | 29103-25J-162-01 | 29103-1"-FG-1601-DLHB0-38H-ET | ROSEMOUNT | 3051T | N/A | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1073 | Pressure Transmitter | NATURAL GAS | PAD A S07 NG INJECTION PRESSURE | 29103-25J-171-01 | 29103-1"-FG-1703-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884550 | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1077 | Pressure Transmitter | NATURAL GAS | PAD A P07 NG INJC PRESSURE | 29103-25J-172-01 | 29103-1"-FG-1701-DLHB0-38H-ET | ROSEMOUNT | 3051T | N/A | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1053 | Pressure Transmitter | NATURAL GAS | PAD A S05 NG INJECTION PRESSURE | 29103-25J-151-01 | 29103-1"-FG-1503-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884554 | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2172 | Pressure Transmitter | INSTRUMENT AIR | INSTRUMENT AIR HEADER PAD A PRESSURE | 29103-25J-001-02 | 29103-3"-IA-002-ALDB0 | N/A | N/A | N/A | 0 - 1500 kPa-g | 100 - 2000 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01

## Transmitter Log 200
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature
N |  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1014 | Pressure Transmitter | PRODUCED EMULSION | PAD A P01 PRODUCED EMULSION PRES | 29103-25J-112-01 | 29103-4"-PE-1101-DAPC0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884781 | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 24.1 | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | [52 empty] | Pass | Example row - for reference only. Delete or overwrite before logging real data. | L. Olsen | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2011 | Vortex Flow Meter | STEAM | PAD R S01 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-212-01 | 29103-4"-ST-2100-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2012 | Vortex Flow Meter | STEAM | PAD R S01 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-211-01 | 29103-3"-ST-2101-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2021 | Vortex Flow Meter | STEAM | PAD R S02 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-221-01 | 29103-4"-ST-2200-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2022 | Vortex Flow Meter | STEAM | PAD R S02 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-221-01 | 29103-3"-ST-2201-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2031 | Vortex Flow Meter | STEAM | PAD R S03 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-231-01 | 29103-4"-ST-2300-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2032 | Vortex Flow Meter | STEAM | PAD R S03 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-231-01 | 29103-3"-ST-2301-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2041 | Vortex Flow Meter | STEAM | PAD R S04 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-241-01 | 29103-4"-ST-2400-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2042 | Vortex Flow Meter | STEAM | PAD R S04 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-241-01 | 29103-3"-ST-2401-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.3 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2051 | Vortex Flow Meter | STEAM | PAD R S05 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-251-01 | 29103-4"-ST-2500-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | cc | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2052 | Vortex Flow Meter | STEAM | PAD R S05 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-251-01 | 29103-3"-ST-2501-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2061 | Vortex Flow Meter | STEAM | PAD R S06 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-261-01 | 29103-4"-ST-2600-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2062 | Vortex Flow Meter | STEAM | PAD R S06 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-261-01 | 29103-3"-ST-2601-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2071 | Vortex Flow Meter | STEAM | PAD R S07 HP STM TO INJC WELL TOE FLOW CTRL | 29103-25J-271-01 | 29103-4"-ST-2700-DASSBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2072 | Vortex Flow Meter | STEAM | PAD R S07 HP STM TO INJC WELL HEEL FLOW CTRL | 29103-25J-271-01 | 29103-3"-ST-2701-DASBO-64H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0-15,000 kg/h | 765-38273 kg/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2200 | Pressure Transmitter | STEAM | PAD R HP STEAM TO WELL PAD | 29103-25J-206-01 | 29103-16"-ST-2802-DASB0-90H | ROSEMOUNT | 3051T |  | 0 - 10000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2201 | Pressure Transmitter | STEAM | PAD R HP STEAM TO WELL PAD | 29103-25J-206-01 | 29103-16"-ST-2802-DASB0-90H | ROSEMOUNT | 3051T |  | 0 - 10000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2202 | Pressure Transmitter | STEAM | PAD R HP STEAM FROM FLOWLINE | 29103-25J-206-01 | 29103-16"-ST-2802-DASB0-90H | ROSEMOUNT | 3051T |  | 0 - 10000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2100 | Pressure Transmitter | STEAM | PAD R HP STEAM FROM FLOWLINE | 29103-25J-206-01 | 29103-16"-ST-2800-DASB0-90H | ROSEMOUNT | 3144P |  | -50 - 400ºC | -200 - 600ºC | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2011 | Pressure Transmitter | STEAM | PAD R S01 HP STM TO INJC WELL TOE | 29103-25J-211-01 | 29103-6"-ST-2102-DASB0-64H | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 to 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2012 | Pressure Transmitter | STEAM | PAD R S01 HP STM TO INJC WELL HEEL | 29103-25J-211-01 | 29103-4"-ST-2103-DASB0-64H-ET | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2021 | Pressure Transmitter | STEAM | PAD R S02 HP STM TO INJC WELL TOE | 29103-25J-221-01 | 29103-6"-ST-2202-DASB0-64H | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2022 | Pressure Transmitter | STEAM | PAD R S02 HP STM TO INJC WELL HEEL | 29103-25J-221-01 | 29103-4"-ST-2203-DASB0-64H-ET | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2031 | Pressure Transmitter | STEAM | PAD R S03 HP STM TO INJC WELL TOE | 29103-25J-231-01 | 29103-6"-ST-2302-DASB0-64H | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2032 | Pressure Transmitter | STEAM | PAD R S03 HP STM TO INJC WELL HEEL | 29103-25J-231-01 | 29103-4"-ST-2303-DASB0-64H-ET | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2041 | Pressure Transmitter | STEAM | PAD R S04 HP STM TO INJC WELL TOE | 29103-25J-241-01 | 29103-6"-ST-2402-DASB0-64H | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2042 | Pressure Transmitter | STEAM | PAD R S04 HP STM TO INJC WELL HEEL | 29103-25J-241-01 | 29103-6"-ST-2402-DASB0-64H | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2051 | Pressure Transmitter | STEAM | PAD R S05 HP STM TO INJC WELL TOE | 29103-25J-251-01 | 29103-6"-ST-2502-DASB0-64H | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2052 | Pressure Transmitter | STEAM | PAD R S05 HP STM TO INJC WELL HEEL | 29103-25J-251-01 | 29103-4"-ST-2503-DASB0-64H-ET | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2061 | Pressure Transmitter | STEAM | PAD R S06 HP STM TO INJC WELL TOE | 29103-25J-261-01 | 29103-6"-ST-2602-DASB0-64H | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2062 | Pressure Transmitter | STEAM | PAD R S06 HP STM TO INJC WELL HEEL | 29103-25J-261-01 | 29103-4"-ST-2603-DASB0-64H-ET | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2071 | Pressure Transmitter | STEAM | PAD R S07 HP STM TO INJC WELL TOE | 29103-25J-271-01 | 29103-6"-ST-2702-DASB0-64H | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2072 | Pressure Transmitter | STEAM | PAD R S07 HP STM TO INJC WELL HEEL | 29103-25J-271-01 | 29103-4"-ST-2703-DASB0-64H-ET | ROSEMOUNT | 3051T |  | 0 - 8000 kPa-g | -101 - 27580 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2014 | Pressure Transmitter | PRODUCED EMULSION | PAD R P01 PRODUCED EMULSION PRESSURE | 29103-25J-212-01 | 29103-4"-PE-2101-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.6 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2018 | Pressure Transmitter | PRODUCED GAS | PAD R P01 PRODUCED VAPOR PRESSURE | 29103-25J-212-01 | 29103-4"-PG-2101-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2014 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R P01 PRODUCED EMULSION HEAD | 29103-25J-212-01 | 29103-4"-PE-2101-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.2 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2024 | Pressure Transmitter | PRODUCED EMULSION | PAD R P02 PRODUCED EMULSION PRESSURE | 29103-25J-222-01 | 29103-4"-PE-2201-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2028 | Pressure Transmitter | PRODUCED GAS | PAD R P02 PRODUCED VAPOR PRESSURE | 29103-25J-222-01 | 29103-4"-PG-2201-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2024 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R P02 PRODUCED EMULSION HEAD | 29103-25J-222-01 | 29103-4"-PE-2201-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2034 | Pressure Transmitter | PRODUCED EMULSION | PAD R P03 PRODUCED EMULSION PRESSURE | 29103-25J-232-01 | 29103-4"-PE-2301-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2038 | Pressure Transmitter | PRODUCED GAS | PAD R P03 PRODUCED VAPOR PRESSURE | 29103-25J-232-01 | 29103-4"-PG-2301-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2034 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R P03 PRODUCED EMULSION HEAD | 29103-25J-232-01 | 29103-4"-PE-2301-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2044 | Pressure Transmitter | PRODUCED EMULSION | PAD R P04 PRODUCED EMULSION PRESSURE | 29103-25J-242-01 | 29103-4"-PE-2401-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2048 | Pressure Transmitter | PRODUCED GAS | PAD R P04 PRODUCED VAPOR PRESSURE | 29103-25J-242-01 | 29103-4"-PG-2401-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2044 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R P04 PRODUCED EMULSION HEAD | 29103-25J-242-01 | 29103-4"-PE-2401-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2054 | Pressure Transmitter | PRODUCED EMULSION | PAD R P05 PRODUCED EMULSION PRESSURE | 29103-25J-252-01 | 29103-4"-PE-2501-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2058 | Pressure Transmitter | PRODUCED GAS | PAD R P05 PRODUCED VAPOR PRESSURE | 29103-25J-252-01 | 29103-4"-PG-2501-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2054 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R P05 PRODUCED EMULSION HEAD | 29103-25J-252-01 | 29103-4"-PE-2501-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2064 | Pressure Transmitter | PRODUCED EMULSION | PAD R P06 PRODUCED EMULSION PRESSURE | 29103-25J-262-01 | 29103-4"-PE-2601-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2068 | Pressure Transmitter | PRODUCED GAS | PAD R P06 PRODUCED VAPOR PRESSURE | 29103-25J-262-01 | 29103-4"-PG-2601-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2064 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R P06 PRODUCED EMULSION HEAD | 29103-25J-262-01 | 29103-4"-PE-2601-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2074 | Pressure Transmitter | PRODUCED EMULSION | PAD R P07 PRODUCED EMULSION PRESSURE | 29103-25J-272-01 | 29103-4"-PE-2701-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 6000 kPa-g | -101 - 27580 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2078 | Pressure Transmitter | PRODUCED GAS | PAD R P07 PRODUCED VAPOR PRESSURE | 29103-25J-272-01 | 29103-4"-PG-2701-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 1500 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2074 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R P07 PRODUCED EMULSION HEAD | 29103-25J-272-01 | 29103-4"-PE-2701-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.3 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2014 | Coriolis Flow Meter | PRODUCED EMULSION | PAD R P01 PRODUCED EMULSION FLOW | 29103-25J-211-01 | 29103-4"-PE-2101-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 |  | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2024 | Coriolis Flow Meter | PRODUCED EMULSION | PAD R P02 PRODUCED EMULSION FLOW | 29103-25J-221-01 | 29103-4"-PE-2201-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 |  | 0 to 30 m3/h @flow | 1.82 to 90.91 m3/h @flow | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2034 | Coriolis Flow Meter | PRODUCED EMULSION | PAD R P03 PRODUCED EMULSION FLOW | 29103-25J-231-01 | 29103-4"-PE-2301-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 |  | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2044 | Coriolis Flow Meter | PRODUCED EMULSION | PAD R P05 PRODUCED EMULSION FLOW | 29103-25J-241-01 | 29103-4"-PE-2501-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 |  | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2054 | Coriolis Flow Meter | PRODUCED EMULSION | PAD R P05 PRODUCED EMULSION FLOW | 29103-25J-251-01 | 29103-4"-PE-2601-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 |  | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2064 | Coriolis Flow Meter | PRODUCED EMULSION | PAD R P06 PRODUCED EMULSION FLOW | 29103-25J-261-01 | 29103-4"-PE-2601-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 |  | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2074 | Coriolis Flow Meter | PRODUCED EMULSION | PAD R P07 PRODUCED EMULSION FLOW | 29103-25J-271-01 | 29103-4"-PE-2701-DAPCO-64H-ET | KROHNE | VE544H17420010400004C6 |  | 0-50 M3/h | 0.7-140 M3/h | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2010A | Temperature Transmitter | PRODUCED EMULSION | PAD R P01 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-212-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2010J | Temperature Transmitter | PRODUCED EMULSION | PAD R P01 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-212-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2020A | Temperature Transmitter | PRODUCED EMULSION | PAD R P02 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-222-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2020J | Temperature Transmitter | PRODUCED EMULSION | PAD R P02 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-222-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2030A | Temperature Transmitter | PRODUCED EMULSION | PAD R P03 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-232-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2030J | Temperature Transmitter | PRODUCED EMULSION | PAD R P03 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-232-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2040A | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD R P04 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-242-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2040J | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD R P04 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-242-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2050A | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD R P05 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-252-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2050J | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD R P05 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-252-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2060A | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD R P06 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-262-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2060J | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD R P06 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-262-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2070J | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD R P07 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-272-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2070A | TEMPERATURE TRANSMITTER | PRODUCED EMULSION | PAD R P07 PROD WELL DOWNHOLE TEMPERATURE | 29103-25J-272-01 | N/A | ROSEMOUNT | 644HAK6J6M5C8Q4DA1K1005 |  | 0 - 350°C | -180 - 1372°C | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2015 | Pressure Transmitter | PRODUCED EMULSION | PAD R S01 RETURN FLUID TO PROD WELL HEAD | 29103-25J-212-01 | 29103-4"-P-2101-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2015 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R S01 RETURN FLUID TO PROD WELL HEADER | 29103-25J-212-01 | 29103-4"-P-2101-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.6 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2025 | Pressure Transmitter | PRODUCED EMULSION | PAD R S02 RETURN FLUID TO PROD WELL HEAD | 29103-25J-222-01 | 29103-4"-P-2201-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2025 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R S02 RETURN FLUID TO PROD WELL HEADER | 29103-25J-222-01 | 29103-4"-P-2201-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2035 | Pressure Transmitter | PRODUCED EMULSION | PAD R S03 RETURN FLUID TO PROD WELL HEAD | 29103-25J-232-01 | 29103-4"-P-2301-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2035 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R S03 RETURN FLUID TO PROD WELL HEADER | 29103-25J-232-01 | 29103-4"-P-2301-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2045 | Pressure Transmitter | PRODUCED EMULSION | PAD R S04 RETURN FLUID TO PROD WELL HEAD | 29103-25J-242-01 | 29103-4"-P-2401-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2045 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R S04 RETURN FLUID TO PROD WELL HEADER | 29103-25J-242-01 | 29103-4"-P-2401-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.6 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2055 | Pressure Transmitter | PRODUCED EMULSION | PAD R S05 RETURN FLUID TO PROD WELL HEAD | 29103-25J-252-01 | 29103-4"-P-2501-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.9 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2055 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R S05 RETURN FLUID TO PROD WELL HEADER | 29103-25J-252-01 | 29103-4"-P-2501-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2065 | Pressure Transmitter | PRODUCED EMULSION | PAD R S06 RETURN FLUID TO PROD WELL HEAD | 29103-25J-262-01 | 29103-4"-P-2601-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2065 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R S06 RETURN FLUID TO PROD WELL HEADER | 29103-25J-262-01 | 29103-4"-P-2601-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2075 | Pressure Transmitter | PRODUCED EMULSION | PAD R S07 RETURN FLUID TO PROD WELL HEAD | 29103-25J-272-01 | 29103-4"-P-2701-DAPC0-64H-ET | ROSEMOUNT | 3051TG4A2B21AS1M536Q4Q8Q15P1BR5 |  | 0 - 3000 kPa-g | -101 - 5515 kPa-g | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-2075 | Temperature Indicating Transmitter | PRODUCED EMULSION | PAD R S07 RETURN FLUID TO PROD WELL HEADER | 29103-25J-272-01 | 29103-4"-P-2701-DAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA |  | -50 - 300°C | -200 - 600°C | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | FLUKE | 1551A EX | 6627011 | '2026-05-13 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2015 | Vortex Flow Meter | NATURAL GAS | PAD R S01 NG TO INJC WELL TOE FLOW CTRL | 29103-25J-211-01 | 29103-1"-FG-2105-DLHB0-38H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0 to 30 m3/h @flow | 1.82 to 90.91 m3/h @flow | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2035 | Vortex Flow Meter | NATURAL GAS | PAD R S03 NG TO INJC WELL TOE FLOW CTRL | 29103-25J-231-01 | 29103-1"-FG-2305-DLHB0-38H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0 to 30 m3/h @flow | 1.82 to 90.91 m3/h @flow | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-2055 | Vortex Flow Meter | NATURAL GAS | PAD R S05 NG TO INJC WELL TOE FLOW CTRL | 29103-25J-251-01 | 29103-1"-FG-2505-DLHB0-38H | ROSEMOUNT | 8800DF010SA8N1D1K6M5Q5Q8Q66Q71Q77 |  | 0 to 30 m3/h @flow | 1.82 to 90.91 m3/h @flow | N/A | Yes | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | EMERSON | TREX | 210100082367 | '2026-07-31 | [50 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2013 | Pressure Transmitter | NATURAL GAS | PAD R S01 NG INJECTION PRESSURE | 29103-25J-211-01 | 29103-1"-FG-2103-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 to 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2017 | Pressure Transmitter | NATURAL GAS | PAD R P01 NG INJC PRESSURE | 29103-25J-212-01 | 29103-1"-FG-2101-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2023 | Pressure Transmitter | NATURAL GAS | PAD R S02 NG INJECTION PRESSURE | 29103-25J-221-01 | 29103-1"-FG-2203-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2027 | Pressure Transmitter | NATURAL GAS | PAD R P02 NG INJC PRESSURE | 29103-25J-222-01 | 29103-1"-FG-2201-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2033 | Pressure Transmitter | NATURAL GAS | PAD R S03 NG INJECTION PRESSURE | 29103-25J-231-01 | 29103-1"-FG-2303-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2037 | Pressure Transmitter | NATURAL GAS | PAD R P03 NG INJC PRESSURE | 29103-25J-232-01 | 29103-1"-FG-2301-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2043 | Pressure Transmitter | NATURAL GAS | PAD R S04 NG INJECTION PRESSURE | 29103-25J-241-01 | 29103-1"-FG-2403-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2047 | Pressure Transmitter | NATURAL GAS | PAD R P04 NG INJC PRESSURE | 29103-25J-242-01 | 29103-1"-FG-2401-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2057 | Pressure Transmitter | NATURAL GAS | PAD R P05 NG INJC PRESSURE | 29103-25J-252-01 | 29103-1"-FG-2501-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2063 | Pressure Transmitter | NATURAL GAS | PAD R S06 NG INJECTION PRESSURE | 29103-25J-261-01 | 29103-1"-FG-2603-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2067 | Pressure Transmitter | NATURAL GAS | PAD R P06 NG INJC PRESSURE | 29103-25J-262-01 | 29103-1"-FG-2601-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2073 | Pressure Transmitter | NATURAL GAS | PAD R S07 NG INJECTION PRESSURE | 29103-25J-271-01 | 29103-1"-FG-2703-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2077 | Pressure Transmitter | NATURAL GAS | PAD R P07 NG INJC PRESSURE | 29103-25J-272-01 | 29103-1"-FG-2701-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2053 | Pressure Transmitter | NATURAL GAS | PAD R S05 NG INJECTION PRESSURE | 29103-25J-251-01 | 29103-1"-FG-2503-DLHB0-38H-ET | ROSEMOUNT | 3051T |  | 0 - 4000 kPa-g | -101 - 5515 kPa-g | N/A | YES | 4-20 mA w/ HART | N/A | N/A | LO | LO | LO | LO | N/A | LO | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | CRYSTAL ENGINEERING | IS33-36/5000 PSI | 4530-525617 | '2026-07-02 | EMERSON | TREX | 210100082367 | '2026-07-31 | [46 empty] | Levy Ostrup | '2026-08-01
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2173 | Pressure Transmitter |  | INSTRUMENT AIR HEADER PAD R PRESSURE | 29103-25J-001-03 | 29103-3"-IA-0003-ALDB0 | ROSEMOUNT | 3051T | 26SIPG3884463 | 0 to 1500 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART

## Valve Log 200
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date
N | [5 empty] | 29103-25J-106-01 | 29103-16"-ST-1800-DASB0-90H | 29103-PV-1200 |  | PCV |  | N/A | 51 | CA6NM SS/Nitrided | A487 gr CA6NM HF | N/A | N/A | Inch | 3 | N/A | SVI3 | IV | 1500 | N/A | N/A | 12" | Flanged | N/A | N/A | 0C18929.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-106-01 | 29103-16"-ST-1800-DASB0-90H | 29103-PV-1200 |  | PCV |  | S-26-019797 | 51 | CA6NM SS/Nitrided | A487 gr CA6NM HF | N/A | 41000 | Inch | 3" | F005382540 | SVI3 | IV | 1500 | N/A | N/A | 12 | Flanged | N/A | N/A | 0C18929.52 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-111-01 | 29103-6"-ST-1102-BASB0-64H | 29103-FV-1011 |  | FCV |  | 1000383587 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383579 | P3E HT | Inch | 4" | F005340804 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-111-01 | 29103-3"-ST-1101-DASB0-64H | 29103-FV-1012 |  | FCV |  | 1000383583 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389735 | P25E HT | Inch | 3" | F005340807 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-121-01 | 29103-6"-ST-1202-DASB0-64H | 29103-FV-1021 |  | FCV |  | 1000383602 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383595 | P3E HT | Inch | 4" | F005340829 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-121-01 | 29103-3"-ST-1201-DASB0-64H | 29103-FV-1022 |  | FCV |  | 1000383533 | PDA200 | 5CB TC | TC c/c S17400 carrier | 1000389751 | P25E HT | Inch | 3" | F005209238 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-131-01 | 29103-6"-ST-1302-DASB0-64H | 29103-FV-1031 |  | FCV |  | 1000383588 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383580 | P3E HT | Inch | 4" | F005340815 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-131-01 | 29103-3"-ST-1301-DASB0-64H | 29103-FV-1032 |  | FCV |  | 1000383564 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389736 | P25E HT | Inch | 3" | F005340816 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-141-01 | 29103-6"-ST-1402-DASB0-64H | 29103-FV-1041 |  | FCV |  | 1000383603 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383596 | P3E HT | Inch | 4" | F005340813 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-141-01 | 29103-3"-ST-1401-DASB0-64H | 29103-FV-1042 |  | FCV |  | 1000383534 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389752 | P25E HT | Inch | 3" | F005209236 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-151-01 | 29103-6"-ST-1502-DASB0-64H | 29103-FV-1051 |  | FCV |  | 1000383589 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383581 | P3E HT | Inch | 4" | F005340836 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-151-01 | 29103-3"-ST-1501-DASB0-64H | 29103-FV-1052 |  | FCV |  | 1000383565 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389737 | P25E HT | Inch | 3" | F005340809 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-161-01 | 29103-6"-ST-1602-DASB0-64H | 29103-FV-1061 |  | FCV |  | 1000383604 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383597 | P3E HT | Inch | 4" | F005340803 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-161-01 | 29103-3"-ST-1601-DASB0-64H | 29103-FV-1062 |  | FCV |  | 1000383535 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389753 | P25E HT | Inch | 3" | F005209241 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-171-01 | 29103-6"-ST-1702-DASB0-64H | 29103-FV-1071 |  | FCV |  | 1000383561 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000383583 | P3E HT | Inch | 4" | F005340801 | DVC-6200 | V | 900 | N/A | N/A | 2.15 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | STEAM | 29103-25J-171-01 | 29103-3"-ST-1701-DASB0-64H | 29103-FV-1072 |  | FCV |  | 1000383566 | PDA200 | 5CB TC | TC c/w S17400 carrier | 1000389738 | P25E HT | Inch | 3" | F005340818 | DVC-6200 | V | 900 | N/A | N/A | 1.5 | Flanged | N/A | N/A | 0C00070.2 | [51 empty] | EMERSON | TREX | 210100082367 | '2026-07-31 |  | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-111-01 | 29103-1"-FG-1105-DLHB0-38H-ET | 29103-FV-1015 |  | FCV |  | S-26-018955 | 88 Spring & Diaphragm | 316 SS | 316 SS | N/A | N/A | Inch | 0.8 | F005452608 | SVI3 SMART | IV | 1500 | N/A | N/A | 1 | Flanged | N/A | N/A | 0C18929.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-131-01 | 29103-1"-FG-1305-DLHB0-38H-ET | 29103-FV-1035 |  | FCV |  | N/A | 88 Spring & Diaphragm | 316 SS | 316 SS | N/A | N/A | Inch | 0.8 | N/A | SVI3 SMART | IV | 1500 | N/A | N/A | 1 | Flanged | N/A | N/A | 0C18929.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-151-01 | 29103-1"-FG-1505-DLHB0-38H-ET | 29103-FV-1055 |  | FCV |  | N/A | 88 Spring & Diaphragm | 316 SS | 316 SS | N/A | N/A | Inch | 0.8 | N/A | SVI3 SMART | IV | 1500 | N/A | N/A | 1 | Flanged | N/A | N/A | 0C18929.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-111-01 | 29103-1"-FG-1103-DLHB0-38H-ET | 29103-KV-1013 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224154 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-112-01 | 29103-1"-FG-1101-DLHB0-38H-ET | 29103-KV-1017 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224157 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-121-01 | 29103-1"-FG-1203-DLHB0-38H-ET | 29103-KV-1023 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224155 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-122-01 | 29103-1"-FG-1201-DLHB0-38H-ET | 29103-KV-1027 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224106 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-131-01 | 29103-1"-FG-1303-DLHB0-38H-ET | 29103-KV-1033 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224111 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-132-01 | 29103-1"-FG-1301-DLHB0-38H-ET | 29103-KV-1037 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224153 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-141-01 | 29103-1"-FG-1403-DLHB0-38H-ET | 29103-KV-1043 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224152 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-142-01 | 29103-1"-FG-1401-DLHB0-38H-ET | 29103-KV-1047 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224181 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-151-01 | 29103-1"-FG-1503-DLHB0-38H-ET | 29103-KV-1053 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224113 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-152-01 | 29103-1"-FG-1501-DLHB0-38H-ET | 29103-KV-1057 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224184 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-161-01 | 29103-1"-FG-1603-DLHB0-38H-ET | 29103-KV-1063 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224177 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-162-01 | 29103-1"-FG-1601-DLHB0-38H-ET | 29103-KV-1067 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224175 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-171-01 | 29103-1"-FG-1703-DLHB0-38H-ET | 29103-KV-1073 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224108 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | NATURAL GAS | 29103-25J-172-01 | 29103-1"-FG-1701-DLHB0-38H-ET | 29103-KV-1077 |  | PCV |  | N/A | VPVL100SR4/5BD | 316 SS | Xtreme | 25224148 | 1/2" 4B36HBXTB2 |  |  | N/A | N/A | VI | 800 | N/A | N/A | 1/2" | Threaded | A47713296 | JS2D8314H301-24VDC | 0C7803.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-112-01 | 29103-4"-PE-1101-DAPC0-64H-ET | 29103-PV-1014 |  | PCV |  | 1000383571 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | 1000389743 | P25E | Inch | 1.5 | F005209232 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-122-01 | 29103-4"-PE-1201-DAPC0-64H-ET | 29103-PV-1024 |  | PCV |  | 1000383540 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005209243 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-132-01 | 29103-4"-PE-1301-DAPC0-64H-ET | 29103-PV-1034 |  | PCV |  | 1000383572 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005340817 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-142-01 | 29103-4"-PE-1401-DAPC0-64H-ET | 29103-PV-1044 |  | PCV |  | 1000383541 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005209347 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-152-01 | 29103-4"-PE-1501-DAPC0-64H-ET | 29103-PV-1054 |  | PCV |  | 1000383573 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005340832 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-162-01 | 29103-4"-PE-1601-DAPC0-64H-ET | 29103-PV-1064 |  | PCV |  | 1000383542 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005209242 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-172-01 | 29103-4"-PE-1701-DAPC0-64H-ET | 29103-PV-1074 |  | PCV |  | 1000383574 | 667-46 Spring & Diaphragm | 5CB TC | TC c/w S17400 carrier | N/A | P25E | Inch | 1.5 | F005340799 | DVC6200-PD SMART | V | 900 | N/A | N/A | 3 | Flanged | N/A | N/A | 0C00070.2 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-112-01 | 29103-4"-PE-1102-DAPC0-64H-ET | 29103-XV-1011 |  |  |  | 3656446-011 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129208 | 4TF9RBPA105N |  |  | F005266343 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-112-01 | 29103-4"-PE-1103-DAPC0-64H-ET | 29103-XV-1012 |  |  |  | 3656446-017 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129209 | 4TF9RBPA105N |  |  | F005266334 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-122-01 | 29103-4"-PE-1202-DAPC0-64H-ET | 29103-XV-1021 |  |  |  | 3656446-024 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129210 | 4TF9RBPA105N |  |  | F005266348 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-122-01 | 29103-4"-PE-1203-DAPC0-64H-ET | 29103-XV-1022 |  |  |  | 3656446-003 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129211 | 4TF9RBPA105N |  |  | F005266332 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-132-01 | 29103-4"-PE-1302-DAPC0-64H-ET | 29103-XV-1031 |  |  |  | 3656446-020 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129212 | 4TF9RBPA105N |  |  | F005266353 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-132-01 | 29103-4"-PE-1303-DAPC0-64H-ET | 29103-XV-1032 |  |  |  | 3656446-023 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129213 | 4TF9RBPA105N |  |  | F005266335 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-142-01 | 29103-4"-PE-1402-DAPC0-64H-ET | 29103-XV-1041 |  |  |  | 3656446-018 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129214 | 4TF9RBPA105N |  |  | F005266350 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-142-01 | 29103-4"-PE-1403-DAPC0-64H-ET | 29103-XV-1042 |  |  |  | 3656446-028 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129215 | 4TF9RBPA105N |  |  | F005266333 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-152-01 | 29103-4"-PE-1502-DAPC0-64H-ET | 29103-XV-1051 |  |  |  | 3656446-027 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129216 | 4TF9RBPA105N |  |  | F005266347 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-152-01 | 29103-4"-PE-1503-DAPC0-64H-ET | 29103-XV-1052 |  |  |  | 3656446-021 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129217 | 4TF9RBPA105N |  |  | F005266329 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-162-01 | 29103-4"-PE-1602-DAPC0-64H-ET | 29103-XV-1061 |  |  |  | 3656446-025 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129218 | 4TF9RBPA105N |  |  | F005266349 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-162-01 | 29103-4"-PE-1603-DAPC0-64H-ET | 29103-XV-1062 |  |  |  | 3656446-022 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129219 | 4TF9RBPA105N |  |  | F005266338 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-172-01 | 29103-4"-PE-1702-DAPC0-64H-ET | 29103-XV-1071 |  |  |  | 3656446-008 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129220 | 4TF9RBPA105N |  |  | F005266331 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-172-01 | 29103-4"-PE-1703-DAPC0-64H-ET | 29103-XV-1072 |  |  |  | 3656446-007 | LPC-10A-180L-DA | F51+TCC | F316+TCC | YDFQ25129221 | 4TF9RBPA105N |  |  | F005266325 | DVC-6200 AD | V | 900 | N/A | N/A | 4 | Flanged | N/A | N/A | 0C15284.52 | [56 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-106-01 | 29103-10"-PE-1802-DAPC0-64H-ET | 29103-XV-1520 |  |  |  | 3656469-001 | LPS-25A-485L-FC4-2 | F51+TCC | F316+TCC | YDFQ25129207 | 10TF9RBPA105N |  |  | F005266356 | DVC-6200 AD | V | 900

## Transmitter Index
Row # | Tag | Export? | System | Type

## Valve Index
Row # | Equip # | Export? | System | Valve Type

## Instructions
K1B Well Pad Equipment Inspection Tracker
WHAT'S IN THIS WORKBOOK
- Dashboard: live counts and navigation buttons.
- Transmitter Log / Valve Log: one row per piece of equipment, one column per field on the matching PDF form. Row 4 (shaded yellow) is an example row on each - overwrite or delete it.
- Transmitter Index / Valve Index: a condensed, auto-updating view (Tag, System, Type, Export flag). Click a row number to jump straight to that row in the full log.
EXPORTING TO PDF
This workbook holds the data; two separate Python scripts (from the kits already shared) turn rows into filled PDFs:
python3 export_to_pdf.py "Equipment_Inspection_Tracker.xlsx"
python3 export_valve_to_pdf.py "Equipment_Inspection_Tracker.xlsx"
Each script reads its own sheet ("Transmitter Log" / "Valve Log") from this same file - keep each script, its schema/field_map .py files, its PDF template, and (for the transmitter one) the assets/ signature folder together in the same directory as this workbook.
Useful flags on both scripts: --rows 4,7,12 --all --merge --flatten --suffix "DEV." (valve script also has --sign-date and --no-signature). See each script's --help for the full list.
SYSTEM CLASSIFICATION (valves)
Derived from the Line Number's service code: FG = Natural Gas, PG/PE = Produced Emulsion, ST = Steam, P (alone) = Returning Fluid.
A NOTE ON A FEW ITEMS THAT CAN'T BE AUTO-FILLED
Both PDF forms have some Signature/Date lines with no real digital field behind them on the original documents - those still need a pen or a Bluebeam stamp after exporting. See each kit's own README for the full list of which fields those are.

## DEL Transmitter Log 300 260826 (hidden)
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature

## DEL Valve Log 300 260826 (hidden)
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name

## DEL Transmitter Log 2920 260829 (hidden)
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature

## DEL Valve Log 29203 260829 (hidden)
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date

## Transmitter Log 29103
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature
|  | KINOSIS K1B WELL PAD PROJECT | K1B | CA23007 | 29103-FIT-0916 | VORTEXT FLOWMETER | PRODUCED GAS | MAINLINE SEPARATOR VAPOUR OUTLET | 29103-25J-002-01 | 29103-8"-PG-1903-BAPD0-64H-ET | ROSEMOUNT | 8800DF080LA3N1D1K6M5Q5Q8Q25Q66Q71 |  | 0 to 7500 m³/h @flow | 408.23 to 8853.79 m³/h @flow |  | No | 4-20 mA w/ HART | [82 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-0916 | Temperature Transmitter | PRODUCED GAS | MAINLINE SEPARATOR VAPOUR OUTLET | 29103-25J-002-01 | 29103-8"-PG-1903-BAPD0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26STIC3659823 | -50 to 300 ºC | -200 to 600 ºC |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | N/A | N/A | LO | LO | LO | [68 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-0930 | Temperature Transmitter | PRODUCED GAS | PRODUCED VAPOUR TO MAINLINE SEPARATOR | 29103-25J-005-01 | 29103-12"-P-1920-BAPD0-75H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3659822 | -16 to 180 ºC | -200 to 600 ºC |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | N/A | N/A | LO | LO | LO | [68 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29209-TIT-0930 | Temperature Transmitter | PRODUCED GAS | PRODUCED VAPOUR TO MAINLINE SEPARATOR | 29209-25J-004-01 | 29209-12"-P-6022-BAPD0-75H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26STIC3659818 | -15 to 180 ºC | -200 to 600 ºC |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | N/A | N/A | LO | LO | LO | [68 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-0913A | Vortex Flow Meter | PRODUCED EMULSION | 29103-P-001A DISCHARGE FLOW | 29103-25J-003-01 | 29103-6"-HC-1904-BAPC0-64H-ET | ROSEMOUNT | 8800DR060LA3N1D1K6M5Q5Q8Q25Q66Q71 | 13952706 | 0 to 100 m³/h @flow | 7.26 to 225.3 m³/h @flow |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | N/A | N/A | LO | LO | LO | [68 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-0913B | Vortex Flow Meter | PRODUCED EMULSION | 29103-P-001B DISCHARGE FLOW | 29103-25J-003-01 | 29103-6"-HC-1907-BAPC0-64H-ET | ROSEMOUNT | 8800DR060LA3N1D1K6M5Q5Q8Q25Q66Q71 | 1395399 | 0 to 100 m³/h @flow | 7.26 to 225.3 m³/h @flow |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | N/A | N/A | LO | LO | LO | [68 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-FIT-0916 | Vortex Flow Meter | PRODUCED GAS | MAINLINE SEPARATOR VAPOUR OUTLET | 29103-25J-002-01 | 29103-8"-PG-1903-BAPD0-64H-ET | ROSEMOUNT | 8800DF080LA3N1D1K6M5Q5Q8Q25Q66Q71 | 21413125 | 0 to 7500 m³/h @flow | 408.23 to 8853.79 m³/h @flow |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | N/A | N/A | LO | LO | LO | [68 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-LIT-0957A | Guided Wave Radar Level Transmitter |  | 29103-V-004 MAINLINE SEPARATOR | 29103-25J-002-01 |  | ROSEMOUNT | 5301HA1P2N4BM00238BBE6M1P1C1Q4Q8J1Q76N2 (TXMT Model No.) | 25GORD0808548 | 25 to 2055 mm From Probe Tip | 70 to 2100 mm From Vessel Bottom |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-LIT-0957B | Guided Wave Radar Level Transmitter |  | 29103-V-004 MAINLINE SEPARATOR | 29103-25J-002-01 |  | ROSEMOUNT | 5301HA1P2N4BM00238BBE6M1P1C1Q4Q8J1Q76N2 (TXMT Model No.) | 25GORD0808554 | 25 to 2055 mm From Probe Tip | 70 to 2100 mm From Vessel Bottom |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-0900 | Pressure Transmitter | STEAM | PURGE STEAM TO 29103-P-001A/B AND 29103-V-004 | 29103-25J-002-01 | 29103-2"-ST-0002-BASB0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3885634 | 0 to 2000 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-0906 | Pressure Transmitter | PRODUCED EMULSION | 29103-P-001A/B DISCHARGE PRESSURE | 29103-25J-003-01 | 29103-6"-HC-1905-BAPC0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884571 | 0 to 4300 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-0908 | Pressure Transmitter | PRODUCED EMULSION | 29103-P-001A SUCTION PRESSURE | 29103-25J-003-01 | 29103-8"-HC-1903-BAPC0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884664 | 0 to 2000 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-0909 | Pressure Transmitter | PRODUCED EMULSION | 29103-P-001B SUCTION PRESSURE | 29103-25J-003-01 | 29103-8"-HC-1906-BAPC0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884663 | 0 to 2000 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.6 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-2171 | Pressure Transmitter |  | INSTRUMENT AIR HEADER PRESSURE | 29103-25J-001-01 | 29103-3"-IA-0001-ALDB0 | ROSEMOUNT | 3051T | 26SIPG3884465 | 0 to 1500 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-0910 | Pressure Transmitter | PRODUCED EMULSION | 29103-P-001A/B DISCHARGE | 29103-25J-003-01 | 29103-6"-HC-1910-BAPC0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884662 | 0 to 4300 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-0916 | Pressure Transmitter | PRODUCED GAS | MAINLINE SEPARATOR VAPOUR OUTLET | 29103-25J-002-01 | 29103-8"-PG-1903-BAPD0-64H-ET | ROSEMOUNT | 3051T | 26SIPG3884661 | 0 to 1400 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-0906 | Temperature Transmitter | PRODUCED EMULSION | 29103-P-001A/B DISCHARGE TEMPERATURE | 29103-25J-003-01 | 29103-6"-HC-1905-BAPC0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3659824 | -50 to 300 ºC | -200 to 600 ºC |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup

## Valve Log 29103
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | PRODUCED EMULSION | 29103-25J-003-01 | 29103-6"-HC-1905-BAPC0-64H-ET | 29103-LV-0957 |  | LCV |  | S-26-020904 | 88 | CA6NM SS | 316 SS/Stellite |  |  | Inch | 2 |  | SVI3 | IV | 300 |  |  | 3 in | Flanged |  |  |  | 4-20 mA / HART | [55 empty] | Levy Ostrup

## Transmitter Log 29152
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | 29203-TIT-0200A | Temperature Transmitter | HP CONDENSATE | HP STEAM FROM HP STEAM HEADER | 29203-25J-003-01 | 29203-20"-ST-5001-DZSB0-90H | ROSEMOUNT | 3144PD1F1K6M5Q4BR5XA | 26STIC3660231 | -50 to 400 ºC | -200 to 600 ºC |  | Yes | 4-20 mA w/HART | [82 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | CA23007 | KINOSIS K1B | 29203-TIT-0200B | Temperature Transmitter | HP CONDENSATE | HP STEAM CONDENSATE FROM HP STEAM FLOWLINE | 29152-25J-002-01 | 29152-3"-ST-4200-DASB0-64H-ET | ROSEMOUNT | 3144PD1F1K6M5Q4BR5XA | 26STIC3660230 | -50 to 400 ºC | -200 to 600 ºC |  | Yes | 4-20 mA w/HART | [82 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29152-LIT-0203 | Guided Wave Radar Level Transmitter | PRODUCED EMULSION | 29152-T-001 TRUCK OUT TANK | 29152-25J-002-01 |  | ROSEMOUNT | 5301FA1S2F4BM00503CAE6M1P1C1Q4Q8J1Q76N2 (TXMT Model No.) | 25GORD0808551 | 25 to 4562 mm From Probe Tip | 263 to 4800 mm From Tank Bottom |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29152-LIT-0205 | Guided Wave Radar Level Transmitter | HP CONDENSATE | FLOWLINE CONDENSATE BLOWCASE PRESSURE | 29152-25J-001-01 |  | ROSEMOUNT | 5301FA1P2N4BM00093BBE6M1P1C1Q4Q8J1Q76N2 (TXMT Model No.) | 25GORD0808550 | 25 to 655 mm From Probe Tip | 70 to 700 mm From Vessel Bottom |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29152-PIT-0205 | Pressure Transmitter | HP CONDENSATE | FLOWLINE CONDENSATE BLOWCASE PRESSURE | 29152-25J-001-01 |  | ROSEMOUNT | 3051T | 26SIPG3884530 | 0 to 3200 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.5 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29152-PIT-0206 | Pressure Transmitter | NATURAL GAS | 29152-PSV-0207 UPSTREAM PRESSURE | 29152-25J-001-01 | 29152-2"-FG-4202-BAPC0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884505 | 0 to 4000 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup

## Valve Log 29152
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date

## Transmitter Log 29151
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29151-LIT-0103 | Guided Wave Radar Level Transmitter | PRODUCED EMULSION | 29151-T-001 FIELD DRAIN TANK | 29151-25J-002-01 |  | ROSEMOUNT | 5301HA1S2F4BM00503CAE6M1P1C1Q4Q8J1Q76N2 (Model No.) | 25GORD0808553 | 25 to 4562 mm From Probe Tip | 263 to 4800 mm From Tank Bottom |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.8 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29151-LIT-0105 | Guided Wave Radar Level Transmitter | PRODUCED GAS | PRODUCED VAPOUR CONDENSATE BLOWCASE | 29151-25J-001-01 |  | ROSEMOUNT | 5301HA1P2N4BM00093BBE6M1P1C1Q4Q8J1Q76N2 (TXMT Model No.) | 25GORD0808552 | 25 to 655 mm From Probe Tip | 70 to 700 mm From Vessel Bottom |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.6 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29151-PIT-0105 | Pressure Transmitter | PRODUCED GAS | PRODUCED VAPOUR CONDENSATE BLOWCASE PRESSURE | 29151-25J-001-01 |  | ROSEMOUNT | 3051T | 26SIPG3884537 | 0 to 3200 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.7 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup

## Valve Log 29151
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date

## DEL Transmitter Log 1 260830 (hidden)
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature

## DEL Valve Log 1 260830 (hidden)
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date

## Transmitter Log 29203
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29203-TIT-0100B | Temperature Transmitter |  | HP STEAM CONDENSATE FROM HP STEAM FLOWLINE | 29151-25J-002-01 | 29151-3"-ST-4100-DASB0-64H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3660212 | -50 to 400 ºC | -200 to 600 ºC |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29203-LIT-0210 | Level Transmitter |  | PRODUCED VAPOUR CONDENSATE | 29203-25J-002-01 | 29203-10"-HC-5005-BAPD0-64H-ET | ROSEMOUNT | 3051C | 26SIPG3885354 | -2891 to -513 mmH2O 4ºC | -250 to 250 inH2O |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29203-LIT-0220 | Level Transmitter |  | PRODUCED VAPOUR CONDENSATE | 29203-25J-002-01 | 29203-10"-HC-5009-BAPD0-64H-ET | ROSEMOUNT | 3051C |  | -2891 to -513 mmH2O 4ºC | -250 to 250 inH2O |  | Yes
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29203-LIT-0221 | Level Transmitter |  | HP STEAM CONDENSATE TO DRAIN AREA 2 | 29203-25J-003-01 | 29203-10"-ST-5004-DASB0-75H-ET | ROSEMOUNT | 3051C |  | -1565 to -610 mmH2O 4ºC | -250 to 250 inH2O |  | Yes | [19 empty] | N/A
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29203-LIT-0211 | Level Transmitter |  | HP STEM CONDENSATE TO DRAIN AREA 1 | 29203-25J-003-01 | 29203-10"-ST-5005-DASB0-75H-ET | ROSEMOUNT | 3051C | 26SIPG3883448 | -1565 to -610 mmH2O 4ºC | -250 to 250 inH2O |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29203-TIT-0100A | Temperature Transmitter |  | HP STEAM FROM HP STEAM HEADER | 29203-25J-003-01 | 29203-20"-ST-5002-DZSB0-90H | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3660235 | -50 to 400 ºC | -200 to 600 ºC |  | Yes | 4-20 mA / HART

## Valve Log 29203
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date

## Transmitter Log 400
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1520 | Pressure Transmitter |  | PAD A PRODUCED EMULSION TO FLOWLINE | 29103-25J-106-01 | 29103-10"-PE-1802-DAPC0-64H-ET | ROSEMOUNT | 3051T | 26SIPG388726 | 0 to 4000 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1300 | Pressure Transmitter |  | PAD A NATURAL GAS TO DISTRIBUTION HEADER | 29103-25J-106-01 | 29103-2"-FG-1110-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884539 | 0 to 9200 kPa-g | -101 to 27580 kPa-g |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1301 | Pressure Transmitter |  | PAD A NATURAL GAS TO DISTRIBUTION HEADER | 29103-25J-106-01 | 29103-2"-FG-1110-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884538 | 0 to 9200 kPa-g | -101 to 27580 kPa-g |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-1302 | Pressure Transmitter |  | PAD A NATURAL GAS TO DISTRIBUTION HEADER | 29103-25J-106-01 | 29103-2"-FG-1110-DLHB0-38H-ET | ROSEMOUNT | 3051T | 26SIPG3884537 | 0 to 10000 kPa-g | -101 to 27580 kPa-g |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-1300 | Temperature Transmitter | PRODUCED EMULSION | PAD A PRODUCED EMULSION TO FLOWLINE | 29103-25J-106-01 | 29103-2"-FG-1110-DLHB0-38H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITC3660169 | -50 to 100 ºC | -200 to 600 ºC |  | Yes | 4-20 mA / HART |  |  | LO | LO | LO | LO | N/A | N/A | LO | LO | N/A | LO | LO | LO | 23.4 | Pass | N/A | N/A | Pass | Pass | N/A | Pass | N/A | N/A | Pass | Pass | N/A | N/A | [54 empty] | Levy Ostrup

## Valve Log 400
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date

## Transmitter Log 500
Control | Header Info | PART 1 – Project Description |  |  | PART 2 – Transmitter Description | [15 empty] | PART 3 – Visual Inspection | [11 empty] | PART 4 – Procedure | [13 empty] | PART 5 – Test Equipment | [11 empty] | PART 6 – Test Results | [40 empty] | PART 7 – Remarks | PART 8 – Inspected/Approved By
Export to PDF (Y/N) | Customer Ref# | Project | Location | Contract # | Tag | Transmitter Type | System Number | Service | P&ID Number | Line Number | Make | Model | Serial Number | Calibration Range | Instrument Range | Repeatability | Local Display | Signal Type | K-Factor | Scale Factor | 1. Stamped SS instrument tag attached. (Initial/NA) | 2. Stamped SS cable tag attached. (Initial/NA) | 3. Device installed as per P&ID drawings and installation details. (Initial/NA) | 4. Equipment accessible and easy to maintain. (Initial/NA) | 5. Verify impulse line(s) are correctly installed. (Initial/NA) | 6. Manifold/isolation valve(s) conform to data sheets. (Initial/NA) | 7. Wiring polarity correct and properly labeled. (Initial/NA) | 8. Tug test terminations. (Initial/NA) | 9. Perform insulation check on wiring. (Initial/NA) | 10. Check enclosure labeling. (Initial/NA) | 11. Check enclosure mounting/orientation. (Initial/NA) | 12. Check boot and seal(s). (All openings sealed) (Initial/NA) | 1. Power the transmitter and measure the voltage (VDC) | 2. Perform leak check procedure. | 3. Power enclosure heater and verify operations. | 4. Power traced tubing bundle(s) and verify operation. | 5. Disconnect wire (open loop) and verify fault. | 6. Verify local display(s) operational. | 7. Ensure process sensing/impulse lines are open. | 8. Verify signal configuration. | 9. Ensure manifolds are placed back into service position. | 10. Confirm controller action as per loop narrative. | 11. Graphic display matches with function. | 12. Construction QA/QC Documents Verified. | 13. Is loop left energized and ready for service. | 14. Place "pre-commissioned" tag on instrument. | Test Equip 1 - Make | Test Equip 1 - Model | Test Equip 1 - Serial | Test Equip 1 - Calibration Date | Test Equip 2 - Make | Test Equip 2 - Model | Test Equip 2 - Serial | Test Equip 2 - Calibration Date | Test Equip 3 - Make | Test Equip 3 - Model | Test Equip 3 - Serial | Test Equip 3 - Calibration Date | 0% Input Upscale | 0% Input Downscale | 0% Output Upscale | 0% Output Downscale | 0% Local Display Upscale | 0% Local Display Downscale | 0% DCS Display/Units Upscale | 0% DCS Display/Units Downscale | 25% Input Upscale | 25% Input Downscale | 25% Output Upscale | 25% Output Downscale | 25% Local Display Upscale | 25% Local Display Downscale | 25% DCS Display/Units Upscale | 25% DCS Display/Units Downscale | 50% Input Upscale | 50% Input Downscale | 50% Output Upscale | 50% Output Downscale | 50% Local Display Upscale | 50% Local Display Downscale | 50% DCS Display/Units Upscale | 50% DCS Display/Units Downscale | 75% Input Upscale | 75% Input Downscale | 75% Output Upscale | 75% Output Downscale | 75% Local Display Upscale | 75% Local Display Downscale | 75% DCS Display/Units Upscale | 75% DCS Display/Units Downscale | 100% Input Upscale | 100% Input Downscale | 100% Output Upscale | 100% Output Downscale | 100% Local Display Upscale | 100% Local Display Downscale | 100% DCS Display/Units Upscale | 100% DCS Display/Units Downscale | System Results | Remarks | Yanda QA Representative - Name | Yanda QA Representative - Date | Yanda QA Representative - Signature | Client Representative - Name | Client Representative - Date | Client Representative - Signature
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-TIT-0001 | Temperature Transmitter |  | PRODUCED VAPOUR TO MAINLINE AIR COOLER | 29209-25J-004-01 | 29103-16"-P-1004-BAPD0-75H-ET | ROSEMOUNT | 3144PD1A1K6M5Q4C8BR5XA | 26SITN3612933 | -50 to 220 ºC | -200 to 600 ºC |  | Yes | 4-20 mA / HART
|  | K1B WELL PAD PROJECT | KINOSIS K1B | CA23007 | 29103-PIT-0001 | Pressure Transmitter |  | PRODUCED VAPOUR TO MAINLINE AIR COOLER | 29209-25J-004-01 | 29103-16"-P-1004-BAPD0-75H-ET | ROSEMOUNT | 3051T | 26SIPG3884572 | 0 to 1400 kPa-g | -101 to 5515 kPa-g |  | Yes | 4-20 mA / HART

## Valve Log 500
Control | Header | [10 empty] | General Description | [18 empty] | Commissioning Inspection | [21 empty] | Functional Verification Activities | [10 empty] | Positioner / Valve Travel Indication | [17 empty] | Calibration & Configuration Test Equipment Used |  |  |  | Comments | Sign-Off
Export to PDF (Y/N) | Customer Name | Project Name | Contract # | Location | System | P&ID # | Line # | Equip # | Unit # | Valve Type | Valve Type - Other (specify) | Actuator - Serial # | Actuator - Model # | Trim - Plug | Trim - Seat | Valve - Serial # | Valve - Model # | Travel - Unit | Travel - Value | Positioner - Serial # | Positioner - Model # | Class (ANSI Leakage Class) | ANSI Rating | Position Limit - Serial # | Position Limit - Model # | ANSI Rating - Size | Body Style | Solenoid - Serial # | Solenoid - Model # | CRN# | Signal Type | Commissioning Tag # | Voltage | Fuse Rating | Inst. Air Pressure | Bad I/O | Verify Device & Screen Match | SS Device Tag | SS Cable Tag | Calibration Tag | Wire Tagged | Cable & Fittings Inspected | Adequate Service Loop | Polarity Correct & Wire Tug | Heat Traced | Insulated | Tubing & Fittings Inspected | Conforms to Install | Conforms to P&ID | Installed By | Verified By | ASME Code | 1. Blow Down Air Supply at Header, Open and Drain Instrument Regulator (initials, or N/A) | 2. Valve is Sliding Stem: Rotary: Quarter Turn: Throttle: Snap Acting (initials, or N/A) | 3. Verify Fail Position: Valve Fails Open / Valve Fails Closed / Valve Fails Last (initials, or N/A) | 4. Verify Positioner Command Signals: mA / % (initials, or N/A) | 5. Valve and Actuator Strokes Smoothly on Command From DCS/PLC (initials, or N/A) | 6. Verify Open and Close Limit Switches Function and are Displayed Correctly on DCS/PLC (initials, or N/A) | 7. Verify Solenoid Trip and Valve Strokes to Fail Position (initials, or N/A) | 8. Verify Positioner is Returned to IN SERVICE (initials, or N/A) | Valve is Sliding Stem / Type | Verify Fail Position | Verify Positioner Command Signals | Valve Position @ 0% (up) | Valve Position @ 25% (up) | Valve Position @ 50% (up) | Valve Position @ 75% (up) | Valve Position @ 100% | Valve Position @ 75% (down) | Valve Position @ 50% (down) | Valve Position @ 25% (down) | Valve Position @ 0% (down) | mA Input @ 0% (up) | mA Input @ 25% (up) | mA Input @ 50% (up) | mA Input @ 75% (up) | mA Input @ 100% | mA Input @ 75% (down) | mA Input @ 50% (down) | mA Input @ 25% (down) | mA Input @ 0% (down) | Test Equipment - Make | Test Equipment - Model | Test Equipment - Serial# | Test Equipment - Calibration Date | Comments | YANDA QC Representative - Name | YANDA Commissioning Representative - Name | YANDA QC Representative - Date