## EHT-004 Pre-Insulation
Reference transcription of the 19 real hand-filled EHT-004 scans - NOT live tracker data, never auto-imported anywhere. Use this to manually cross-check the app's PDF template/schema against the original scans. 19 page instances, double-independently read and reconciled; 136 field(s) flagged as uncertain or disagreeing between the two read passes (highlighted below) - check those against the original PDF by eye.
Source PDF | Source Page | Customer Name | Project Name | Contract # | Location | Trace # | EHT Controller # | Trace Part # | Panel # | RTD(s) # | Circuit # | Trace Line # | Rev # | 1. EHT Receiving Report has been Completed if required - Result | 1. EHT Receiving Report has been Completed if required - Comments | 2. EHT Tag Matches Part # and drawings - Result | 2. EHT Tag Matches Part # and drawings - Comments | 3. EHT is Routed and Installed as per specifications - Result | 3. EHT is Routed and Installed as per specifications - Comments | 4. RTD's Receiving Report has been Completed if required - Result | 4. RTD's Receiving Report has been Completed if required - Comments | 5. RTD's are installed as per drawing and specification - Result | 5. RTD's are installed as per drawing and specification - Comments | 6. EHT/RTD's Tags are correctly labelled and installed - Result | 6. EHT/RTD's Tags are correctly labelled and installed - Comments | 7. As-built drawings completed and submitted - Result | 7. As-built drawings completed and submitted - Comments | 8. Terminations are complete with correct wire tags - Result | 8. Terminations are complete with correct wire tags - Comments | 9. SR/MI Trace Continuity test passed (Record Resistance) - Result | 9. SR/MI Trace Continuity test passed (Record Resistance) - Comments | 10. EHT/RTD's Released for Insulation - Result | 10. EHT/RTD's Released for Insulation - Comments | Test Equip. Model # | Test Equip. Serial # | Cal. Due Date | SR/MI @ 500 VDC - Reading | SR/MI @ 500 VDC - Passed/Fail | SR/MI @ 1000 VDC - Reading | SR/MI @ 1000 VDC - Passed/Fail | SR/MI @ 2500 VDC - Reading | SR/MI @ 2500 VDC - Passed/Fail | Comments | Yanda Representative - Date (yy/mm/dd) | Yanda Representative - Signature | Client Representative - Date (yy/mm/dd) | Client Representative - Signature | Flagged / Uncertain Fields (double-check these against the scan) | Pass-2 Alternate Reading (where the two independent passes disagreed)
Sharp_Scanner_20260908_122854.pdf | 1 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29203-ET-P65002-1-QWK-1 |  |  | 29152-HTP-001 |  |  |  |  | JF |  | N/A | no tags present | JF |  | N/A |  | N/A |  | N/A | core tags & cable tags needed | JF |  | JF | no tags.. | JF |  | JF | [6 empty] | 2.2 GΩ | Pass |  |  |  | 26/09/05 | Signed |  |  | trace_number; panel_number; checklist_item_6_comments
Sharp_Scanner_20260908_122854.pdf | 2 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29203-ET-PE5002-2 | 29151-HTP-001 | 15HTV1-CT |  | RTD4AL | 020 | [6 empty] | TB |  |  |  | TB | [5 empty] | TB | Missing Tags | 4Ω TB | [6 empty] | 295GΩ | Passed | 385GΩ | Passed | 395GΩ | Passed | [5 empty] | cal_due_date; checklist_item_9_result; checklist_item_3_result; checklist_item_5_result; checklist_item_8_result | checklist_item_9_result = '4GΩ TB'
Sharp_Scanner_20260908_122854.pdf | 3 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29203-ET-ST5001-1 | 29151-HTP-001 | D/325Q3472 |  | RTD4AL | 012 | [6 empty] | TB |  |  |  | TB | [5 empty] | TB | Missing Tags | 30-Ω TB | [6 empty] | 690GΩ | Passed | [9 empty] | trace_part_number; checklist_item_9_result; checklist_item_3_result; checklist_item_5_result; checklist_item_8_result | trace_part_number = 'D/32SQ3472'; checklist_item_9_result = '30Ω TB'
Sharp_Scanner_20260908_122854.pdf | 4 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29203-ET-HC5008-1-3 | 29151-HTP-601 | 10HTV1-CT |  | NA | 08 | [6 empty] | TB |  | NA |  | NA | [5 empty] | TB | Missing Tags | 11-Ω TB | [6 empty] | 11GΩ | Passed | 11GΩ | Passed | 7.8GΩ | Passed | [5 empty] | eht_controller_number; megger_2500_result; checklist_item_3_result; checklist_item_8_result; checklist_item_9_result; circuit_number; trace_part_number | eht_controller_number = '29151-HTP-001'; megger_2500_result = 'Passed.'; checklist_item_3_result = 'TG'; checklist_item_8_result = 'TG'; checklist_item_9_result = '11-Ω TG'
Sharp_Scanner_20260908_122854.pdf | 5 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29203-ET-HC5008-1 | 29151-HTP-001 | 10HTV1-CT |  | RTD4AL | 08 | [6 empty] | TB |  | NA |  | TB NA | [5 empty] | TB | Missing Tags | 30Ω TB | [6 empty] | 870GΩ | Passed | 2.2TΩ | Passed | 2.2TΩ | Passed. | added a splice kit |  |  |  |  | checklist_item_3_result; checklist_item_5_result; checklist_item_8_result; checklist_item_9_result
Sharp_Scanner_20260908_122854.pdf | 6 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29203-ET-HC5008-1-2 | 29151-HTP-001 | 10 HTV1-CT |  | NA | 08 | [6 empty] | TB |  | NA |  | NA | [5 empty] | TB | Missing tags | 11Ω TB | [6 empty] | 585GΩ | Passed | 715GΩ | Passed | 800GΩ | Passed | [5 empty] | checklist_item_3_result; checklist_item_8_result; checklist_item_9_result; trace_part_number
Sharp_Scanner_20260908_122854.pdf | 7 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-ST1403-1-3 | [7 empty] | N/A |  | df |  | JF |  | WA |  | N/A |  | df |  | N/A |  | N/A |  | JF |  | N/A |  |  |  |  | (illegible - overwritten/scratched-out scribble in black and blue ink) |  | 2.2 GΩ | Pass. |  |  |  | 26/09/03. |  |  |  | megger_500_reading; yanda_rep_date; checklist_item_2_result; checklist_item_4_result; checklist_item_6_result | megger_500_reading = '[illegible scribble]'; yanda_rep_date = '26/09/03'; checklist_item_2_result = 'JF'; checklist_item_4_result = 'N/A'; checklist_item_6_result = 'JF'
Sharp_Scanner_20260908_122854.pdf | 8 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103.ET-ST1503-1~1 | [7 empty] | NA |  | JF |  | JF |  | NA |  | NA. |  | JF |  | NA. |  | NA |  | JF |  | NA. |  |  |  |  | 2.2G | Pass | 2.2G | Pass |  |  |  | 26/09/03. | Signed |  |  | trace_number; megger_500_reading; yanda_rep_date; yanda_rep_signed; checklist_item_1_result; checklist_item_4_result; checklist_item_5_result; checklist_item_7_result; checklist_item_8_result; checklist_item_10_result; megger_500_result; megger_1000_result | trace_number = '29103-ET-ST1503-1~1'; megger_500_reading = 'illegible'; yanda_rep_date = '26/09/03'; checklist_item_1_result = 'N/A'; checklist_item_4_result = 'N/A'; checklist_item_5_result = 'N/A'; checklist_item_7_result = 'N/A'; checklist_item_8_result = 'N/A'; checklist_item_10_result = 'N/A'
Sharp_Scanner_20260908_122854.pdf | 9 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-ST1403-1-3 | [7 empty] | NA |  | JF |  | JF |  | NA |  | NA |  | JF |  | NA |  | NA |  | JF |  | NA. |  |  |  |  | 2.2GΩ (crossed out) |  | 2.2GΩ | Pass |  |  |  | 26/09/03 | Signed |  |  | trace_number; megger_500_reading; checklist_item_6_result; checklist_item_2_result; checklist_item_3_result; checklist_item_4_result; checklist_item_9_result | trace_number = '29103-ET-ST1303-1-3'; megger_500_reading = '2.2GΩ (written then struck through)'; checklist_item_6_result = 'JA'
Sharp_Scanner_20260908_122854.pdf | 10 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-ST1203-1-3 | [7 empty] | N/A |  | Jf |  | Jf |  | N/A |  | N/A |  | Jf |  | N/A |  | N/A |  | Jf |  | N/A |  |  |  |  | 2.2GΩ (written then crossed out with strikethrough) |  | 2.2GΩ | Pass |  |  |  | 26/09/03 | Signed |  |  | megger_500_reading; checklist_item_2_result; checklist_item_3_result; checklist_item_6_result; checklist_item_9_result | megger_500_reading = '2.2GΩ (crossed out / struck through)'; checklist_item_2_result = 'JT'; checklist_item_3_result = 'JT'; checklist_item_6_result = 'JT'; checklist_item_9_result = 'JT'
Sharp_Scanner_20260908_122854.pdf | 11 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-ST1103-1-3 | [7 empty] | N/A |  | JF |  | JF |  | N/A |  | N/A |  | JF |  | N/A |  | N/A |  | JF |  | N/A |  |  |  |  | 2.2 GΩ (crossed out) | Pass (crossed out) | 2.2 GΩ | Pass |  |  |  | 26/09/03 | Signed |  |  | megger_500_reading; megger_500_result; megger_1000_result
Sharp_Scanner_20260908_122854.pdf | 12 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-ST1703-1-3 | [7 empty] | N/A | Yes JF | JT |  | JT |  | N/A |  | N/A |  | JT |  | N/A |  | N/A | Not Termed / No Core Markers | JT |  | N/A | [6 empty] | 535 MΩ | Pass |  |  |  | 26/09/03 | Signed |  |  | trace_number; checklist_item_2_result; checklist_item_3_result; checklist_item_6_result; checklist_item_9_result; megger_1000_reading | trace_number = '29103-ET-ST1703.1-3'; checklist_item_2_result = 'JH'; checklist_item_3_result = 'JH'; checklist_item_6_result = 'JH'; checklist_item_9_result = 'JH'
Sharp_Scanner_20260908_122854.pdf | 13 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-ST1603-1-3 | [7 empty] | NA |  | JF |  | JF |  | NA |  | NA |  | JF |  | NA |  | NA |  | JF |  | NA | [6 empty] | 278MΩ | Pass |  |  |  | 26/09/03 | Signed |  |  | megger_1000_reading; checklist_item_2_result; checklist_item_3_result; checklist_item_6_result; checklist_item_9_result; trace_number | megger_1000_reading = '278 MΩ'; checklist_item_2_result = 'TF'; checklist_item_3_result = 'TF'; checklist_item_6_result = 'TF'; checklist_item_9_result = 'TF'
Sharp_Scanner_20260908_123001_1.pdf | 3 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-PE1701-2-2 | HTC-16 | D/32SQ3200 | 29103-HTP-003 | 29103-ET-PE1701-2-R-2 | 16 | 1B | 1A1 |  |  | D.E |  | D.E |  |  | N.C |  | N.C | D.E | RTD N.C |  |  |  | N.C | D.E | 114 Ω |  |  | FLUKE | 6344 0088 | July 10, 26 |  | ) | 2.5 GΩ | PASS |  |  | Power kit (JB) missing TAG RTD missing Tag | 26/09/07 | Signed |  |  | circuit_number; test_equip_serial; comments; rtds_number; megger_500_result; checklist_item_2_result; checklist_item_3_result; checklist_item_6_result; checklist_item_9_result | circuit_number = 'CB16'; test_equip_serial = '63440088'; comments = 'powerkit (JB) missing TAG\nRTD missing Tag'
Sharp_Scanner_20260908_123001_1.pdf | 4 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-PE1101-2-2 | HTC-20 | D132SB2114 | 29103-HTP-002 | 29103-ET-PE1101-2-R-2 | 20 | 2B | 1A3 |  |  | D.E |  | D.E |  |  | N.C |  | N.C | D.E | RTD(N.C) |  |  |  | N.C | D.E | 114.5 Ω |  |  | FLUKE | 63440088 | July,10,26 |  |  | 2.26 Ω | PASS |  |  | Broken clasp on JB [closing mechanism] | 26/09/07 | Signed |  |  | eht_controller_number; rtds_number; test_equip_serial; cal_due_date; megger_1000_reading; comments; checklist_item_6_comments; checklist_item_2_result; checklist_item_3_result; checklist_item_6_result; checklist_item_9_result; checklist_item_9_comments; rev | eht_controller_number = 'HTC-70'; rtds_number = '29103-ET-PE1101-2-Q-2'; test_equip_serial = '63440686'; cal_due_date = 'July 10, 26'; megger_1000_reading = '2.26 MΩ'; comments = 'Broken clasp on JB [closure mechanism]'; checklist_item_6_comments = 'RTD (N.C)'
Sharp_Scanner_20260908_123001_1.pdf | 5 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-PE1301-2-2 | HTC-07 | D32 | 29103-HTP-002 | RTD4AL / RTD10-T | CB07 | 1B | 1A1 |  |  | D.E |  | D.E | [5 empty] | D.E | NO TAG ON RTD | D.E |  |  | N.C | D.E | 114.6 Ω |  |  | FLUKE | 63440088 | July 10, 26 |  |  | 2.2 GΩ | PASS |  |  | missing steel ty-wrap on label | 26/09/07 | Signed |  |  | rtds_number; cal_due_date; megger_1000_reading; checklist_item_2_result; checklist_item_4_result; circuit_number; checklist_item_6_result; checklist_item_7_result; checklist_item_9_result; test_equip_serial; comments; checklist_item_3_result; checklist_item_8_comments; checklist_item_9_comments; rev | rtds_number = 'RTD4AL / RTD10-1'; cal_due_date = '24/10/26'; megger_1000_reading = '226 Ω'; checklist_item_4_result = 'D.E'
Sharp_Scanner_20260908_123001_1.pdf | 6 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-PE1401-2-2 | HTC-30 | D132SB2114 | 29103-HTP-003 | 29103-ET-PE1401-2-R-2 | CB-30 | 1B | 1A3 |  |  | D.G | missing RTD M6 | D.G |  |  | Not complete |  | Not complete | D.G | KT TAG Missing | D.G |  |  | Not complete | D.G | 114.7 Ω |  |  | FLUKE | 6344 00BB | July 10, 26 |  |  | 2.2 GΩ | PASS |  |  |  | 26/09/07 | Signed |  |  | trace_part_number; circuit_number; test_equip_serial; cal_due_date; checklist_item_2_result; checklist_item_3_result; checklist_item_6_result; checklist_item_6_comments; checklist_item_7_result; checklist_item_9_result | trace_part_number = 'D1325B2114'; circuit_number = 'CB30'; test_equip_serial = '63440088'; cal_due_date = 'Jul.10/26'; checklist_item_2_result = 'DG'; checklist_item_3_result = 'DG'; checklist_item_6_result = 'DG'; checklist_item_6_comments = 'Not RTD TAG Missing'; checklist_item_7_result = 'DG'; checklist_item_9_result = 'DG'
Sharp_Scanner_20260908_123001_1.pdf | 7 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-PE1501-2-2 | HTC-07 | D/32SB2114 | 29103-HTP-003 | 29103-ET-PE1501-2-R-2 | EB07 | 1B | 1A1 |  |  | De |  | De |  |  | N.C |  | N.C |  | N.C |  |  |  | N.C | De | 114.5 Ω |  |  | FLUKE | 63440096 | July 20, 26 |  |  | 2.2 GΩ | PASS |  |  | • needs Tags on RTD • PUT EHT TAGS on properly facing correct side. | 26/09/07 | Signed |  |  | circuit_number; rev; test_equip_serial; cal_due_date; checklist_item_5_comments; test_equip_model; trace_part_number; checklist_item_2_result; checklist_item_3_result; checklist_item_9_result | circuit_number = '07'; rev = '7A7'; test_equip_serial = '63440088'; cal_due_date = 'July 10, 26'; checklist_item_5_comments = 'N,C'
Sharp_Scanner_20260908_123001_1.pdf | 8 | COOEC Canada Ltd. | K1B Well Pad Project | CA23007-SCM-AGC-004 | Module Yard | 29103-ET-PE1601-2-2 | HTC-12 | D/32SB2114 | 29103-HTP-003 | 29103-ET-PE1601-2-R-2 | CB12 | 1B | 1A1 |  |  | D.E |  | D.E |  |  | N.C |  | N.C | D.E | N.C RTD | D.E |  |  | N.C | D.G | 114.2 Ω |  |  | FLUKE | 63414 0098 | July 10/26 |  |  | 2.2 GΩ | PASS |  |  | Cable Tag is missing stainless ty-wrap. | 26/09/07 | Signed |  |  | test_equip_serial; cal_due_date; checklist_item_9_result; circuit_number; checklist_item_7_result; checklist_item_9_comments; megger_1000_reading | test_equip_serial = '63440098'; cal_due_date = 'July 10, 26'; checklist_item_9_result = 'D.E'